## Equipment Summary
Equipment | Count
Header | 1
Chiller | 3
Primary Variable Pump | 3
Condenser Pump | 3
Cooling Tower | 6
Exhaust Fan | 4

## Terminal_Details
Panel No | DDC Number | DDC Model No | Extension No | Extension Model | Port/Terminal | Point Type | Instance ID | Point Description | Equipment Tag | Equipment Grouping | Equipment Type | Status/Command
Panel-1 | DDC-01 | DDC-8044 |  |  | UI-1 | AI | 1 | Outside Air Temp monitoring | OAT | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 | DDC-8044 |  |  | UI-2 | AI | 2 | Outside Air Relative Humidity Monitoring | OARH | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 | DDC-8044 |  |  | UI-3 | AI | 3 | CHW Common Supply Header Temperature | CHW-ST-01 | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 | DDC-8044 |  |  | UI-4 | AI | 4 | CHW Common Return Header Temperature | CHW-RT-01 | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 | DDC-8044 |  |  | UI-5 | AI | 5 | Condenser Water Supply Header Temperature | CDW-ST-01 | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 | DDC-8044 |  |  | UI-6 | AI | 6 | Condenser Water Return Header Temperature | CDW-RT-01 | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 | DDC-8044 |  |  | UI-7 | AI | 7 | Bypass Temperature | BYP-T | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 | DDC-8044 |  |  | UI-8 | AI | 8 | Bypass Modulating Valve Feedback | BYP-VLV-01 | Common Monitoring | Valve | Status
Panel-1 | DDC-01 | DDC-8044 |  |  | AO-1 | AO | 1 | Bypass Modulating Valve Control | BYP-VLV-01 | Common Monitoring | Valve | Command
Panel-1 | DDC-01 | DDC-8044 |  |  | AO-2 | AO | 2 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 | DDC-8044 |  |  | AO-3 | AO | 3 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 | DDC-8044 |  |  | AO-4 | AO | 4 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 | DDC-8044 |  |  | DO-1 | DO | 1 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 | DDC-8044 |  |  | DO-2 | DO | 2 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 | DDC-8044 |  |  | DO-3 | DO | 3 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 | DDC-8044 |  |  | DO-4 | DO | 4 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 |  | Ext Module | IO-V6002 | UI-1 | AI | 9 | CDW Common supply header flow | CDW-SF | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 |  | Ext Module | IO-V6002 | UI-2 | AI | 10 | CHW Common Supply and Return Header Pressure monitoring | CDW-SPRP | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 |  | Ext Module | IO-V6002 | UI-3 | AI | 11 | Diff Pressure Monitoring @Main Header | DPT-01 | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 |  | Ext Module | IO-V6002 | UI-4 | AI | 12 | Diff Pressure Monitoring @AHU Header | DPT-02 | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 |  | Ext Module | IO-V6002 | UI-5 | AI | 13 | Decimal Meter | DM | Common Monitoring | Sensor | Status
Panel-1 | DDC-01 |  | Ext Module | IO-V6002 | UI-6 | DI | 9 | Chiller-1 Run Status | CH-01 | Water Cooled Chillers | Chiller | Status
Panel-1 | DDC-01 |  | Ext Module | IO-V6002 | DO-1 | DO | 5 | Chiller-1 Enable/Disable Command | CH-01 | Water Cooled Chillers | Chiller | Command
Panel-1 | DDC-01 |  | Ext Module | IO-V6002 | DO-2 | DO | 6 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 |  | IO Module-01 | IO-0800-485 | DI-1 | DI | 1 | Chiller-1 Auto/Manual Status | CH-01 | Water Cooled Chillers | Chiller | Status
Panel-1 | DDC-01 |  | IO Module-01 | IO-0800-485 | DI-2 | DI | 2 | Chiller-2 Auto/Manual Status | CH-02 | Water Cooled Chillers | Chiller | Status
Panel-1 | DDC-01 |  | IO Module-01 | IO-0800-485 | DI-3 | DI | 3 | Chiller-3 Auto/Manual Status | CH-03 | Water Cooled Chillers | Chiller | Status
Panel-1 | DDC-01 |  | IO Module-01 | IO-0800-485 | DI-4 | DI | 4 | Chiller-1 Fault/Alarm Status | CH-01 | Water Cooled Chillers | Chiller | Status
Panel-1 | DDC-01 |  | IO Module-01 | IO-0800-485 | DI-5 | DI | 5 | Chiller-2 Fault/Alarm Status | CH-02 | Water Cooled Chillers | Chiller | Status
Panel-1 | DDC-01 |  | IO Module-01 | IO-0800-485 | DI-6 | DI | 6 | Chiller-3 Fault/Alarm Status | CH-03 | Water Cooled Chillers | Chiller | Status
Panel-1 | DDC-01 |  | IO Module-01 | IO-0800-485 | DI-7 | DI | 7 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 |  | IO Module-01 | IO-0800-485 | DI-8 | DI | 8 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-01 |  | IO Module-02 | IO-0800-485 | DI-1 | DI | 1 | Chiller-1 Motorized Valve-1 Feedback | CH-01-VLV-01 | Water Cooled Chillers | Valve | Status
Panel-1 | DDC-01 |  | IO Module-02 | IO-0800-485 | DI-2 | DI | 2 | Chiller-1 Motorized Valve-2 Feedback | CH-01-VLV-02 | Water Cooled Chillers | Valve | Status
Panel-1 | DDC-01 |  | IO Module-02 | IO-0800-485 | DI-3 | DI | 3 | Chiller-2 Motorized Valve-1 Feedback | CH-02-VLV-01 | Water Cooled Chillers | Valve | Status
Panel-1 | DDC-01 |  | IO Module-02 | IO-0800-485 | DI-4 | DI | 4 | Chiller-2 Motorized Valve-2 Feedback | CH-02-VLV-02 | Water Cooled Chillers | Valve | Status
Panel-1 | DDC-01 |  | IO Module-02 | IO-0800-485 | DI-5 | DI | 5 | Chiller-3 Motorized Valve-1 Feedback | CH-03-VLV-01 | Water Cooled Chillers | Valve | Status
Panel-1 | DDC-01 |  | IO Module-02 | IO-0800-485 | DI-6 | DI | 6 | Chiller-3 Motorized Valve-2 Feedback | CH-03-VLV-02 | Water Cooled Chillers | Valve | Status
Panel-1 | DDC-01 |  | IO Module-02 | IO-0800-485 | DI-7 | DI | 7 | Chiller-2 Run Status | CH-02 | Water Cooled Chillers | Chiller | Status
Panel-1 | DDC-01 |  | IO Module-02 | IO-0800-485 | DI-8 | DI | 8 | Chiller-3 Run Status | CH-03 | Water Cooled Chillers | Chiller | Status
Panel-1 | DDC-01 |  | IO Module-03 | IO-0008-485 | DO-1 | DO | 1 | Chiller-1 Motorized Valve-1 Command | CH-01-VLV-01 | Water Cooled Chillers | Valve | Command
Panel-1 | DDC-01 |  | IO Module-03 | IO-0008-485 | DO-2 | DO | 2 | Chiller-1 Motorized Valve-2 Command | CH-01-VLV-02 | Water Cooled Chillers | Valve | Command
Panel-1 | DDC-01 |  | IO Module-03 | IO-0008-485 | DO-3 | DO | 3 | Chiller-2 Motorized Valve-1 Command | CH-02-VLV-01 | Water Cooled Chillers | Valve | Command
Panel-1 | DDC-01 |  | IO Module-03 | IO-0008-485 | DO-4 | DO | 4 | Chiller-2 Motorized Valve-2 Command | CH-02-VLV-02 | Water Cooled Chillers | Valve | Command
Panel-1 | DDC-01 |  | IO Module-03 | IO-0008-485 | DO-5 | DO | 5 | Chiller-3 Motorized Valve-1 Command | CH-03-VLV-01 | Water Cooled Chillers | Valve | Command
Panel-1 | DDC-01 |  | IO Module-03 | IO-0008-485 | DO-6 | DO | 6 | Chiller-3 Motorized Valve-2 Command | CH-03-VLV-02 | Water Cooled Chillers | Valve | Command
Panel-1 | DDC-01 |  | IO Module-03 | IO-0008-485 | DO-7 | DO | 7 | Chiller-2 Enable/Disable Command | CH-02 | Water Cooled Chillers | Chiller | Command
Panel-1 | DDC-01 |  | IO Module-03 | IO-0008-485 | DO-8 | DO | 8 | Chiller-3 Enable/Disable Command | CH-03 | Water Cooled Chillers | Chiller | Command
Panel-1 | DDC-02 | DDC-8044 |  |  | UI-1 | AI | 1 | Chilled Water Pump-1 VFD Feedback | PP-01 | Primary Pumps | VFD | Status
Panel-1 | DDC-02 | DDC-8044 |  |  | UI-2 | AI | 2 | Chilled Water Pump-2 VFD Feedback | PP-02 | Primary Pumps | VFD | Status
Panel-1 | DDC-02 | DDC-8044 |  |  | UI-3 | AI | 3 | Chilled Water Pump-3 VFD Feedback | PP-03 | Primary Pumps | VFD | Status
Panel-1 | DDC-02 | DDC-8044 |  |  | UI-4 | DI | 4 | Chilled Water Pump-1 run Status | PP-01 | Primary Pumps | Pump | Status
Panel-1 | DDC-02 | DDC-8044 |  |  | UI-5 | DI | 5 | Chilled Water Pump-2 run Status | PP-02 | Primary Pumps | Pump | Status
Panel-1 | DDC-02 | DDC-8044 |  |  | UI-6 | DI | 6 | Chilled Water Pump-3 run Status | PP-03 | Primary Pumps | Pump | Status
Panel-1 | DDC-02 | DDC-8044 |  |  | UI-7 | AI | 7 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-02 | DDC-8044 |  |  | UI-8 | AI | 8 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-02 | DDC-8044 |  |  | AO-1 | AO | 1 | Chilled Water Pump-1 VFD Control | PP-01 | Primary Pumps | VFD | Command
Panel-1 | DDC-02 | DDC-8044 |  |  | AO-2 | AO | 2 | Chilled Water Pump-2 VFD Control | PP-02 | Primary Pumps | VFD | Command
Panel-1 | DDC-02 | DDC-8044 |  |  | AO-3 | AO | 3 | Chilled Water Pump-3 VFD Control | PP-03 | Primary Pumps | VFD | Command
Panel-1 | DDC-02 | DDC-8044 |  |  | AO-4 | AO | 4 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-02 | DDC-8044 |  |  | DO-1 | DO | 1 | Chilled Water Pump-1 VFD On/Off Command | PP-01 | Primary Pumps | Pump | Command
Panel-1 | DDC-02 | DDC-8044 |  |  | DO-2 | DO | 2 | Chilled Water Pump-2 VFD On/Off Command | PP-02 | Primary Pumps | Pump | Command
Panel-1 | DDC-02 | DDC-8044 |  |  | DO-3 | DO | 3 | Chilled Water Pump-3 VFD On/Off Command | PP-03 | Primary Pumps | Pump | Command
Panel-1 | DDC-02 | DDC-8044 |  |  | DO-4 | DO | 4 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-02 |  | Ext Module | IO-V0800 | DI-1 | DI | 9 | Chilled Water Pump-1 Trip Status | PP-01 | Primary Pumps | Pump | Status
Panel-1 | DDC-02 |  | Ext Module | IO-V0800 | DI-2 | DI | 10 | Chilled Water Pump-2 Trip Status | PP-02 | Primary Pumps | Pump | Status
Panel-1 | DDC-02 |  | Ext Module | IO-V0800 | DI-3 | DI | 11 | Chilled Water Pump-3 Trip Status | PP-03 | Primary Pumps | Pump | Status
Panel-1 | DDC-02 |  | Ext Module | IO-V0800 | DI-4 | DI | 12 | Chilled Water Pump-1 Auto/Manual Status | PP-01 | Primary Pumps | Pump | Status
Panel-1 | DDC-02 |  | Ext Module | IO-V0800 | DI-5 | DI | 13 | Chilled Water Pump-2 Auto/Manual Status | PP-02 | Primary Pumps | Pump | Status
Panel-1 | DDC-02 |  | Ext Module | IO-V0800 | DI-6 | DI | 14 | Chilled Water Pump-3 Auto/Manual Status | PP-03 | Primary Pumps | Pump | Status
Panel-1 | DDC-02 |  | Ext Module | IO-V0800 | DI-7 | DI | 15 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-02 |  | Ext Module | IO-V0800 | DI-8 | DI | 16 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-03 | DDC-8044 |  |  | UI-1 | AI | 1 | Condenser Water Pump-1 VFD Feedback | CP-01 | Condenser Pumps | VFD | Status
Panel-1 | DDC-03 | DDC-8044 |  |  | UI-2 | AI | 2 | Condenser Water Pump-2 VFD Feedback | CP-02 | Condenser Pumps | VFD | Status
Panel-1 | DDC-03 | DDC-8044 |  |  | UI-3 | AI | 3 | Condenser Water Pump-3 VFD Feedback | CP-03 | Condenser Pumps | VFD | Status
Panel-1 | DDC-03 | DDC-8044 |  |  | UI-4 | DI | 4 | Condenser Water Pump-1 run Status | CP-01 | Condenser Pumps | Pump | Status
Panel-1 | DDC-03 | DDC-8044 |  |  | UI-5 | DI | 5 | Condenser Water Pump-2 run Status | CP-02 | Condenser Pumps | Pump | Status
Panel-1 | DDC-03 | DDC-8044 |  |  | UI-6 | DI | 6 | Condenser Water Pump-3 run Status | CP-03 | Condenser Pumps | Pump | Status
Panel-1 | DDC-03 | DDC-8044 |  |  | UI-7 | AI | 7 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-03 | DDC-8044 |  |  | UI-8 | AI | 8 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-03 | DDC-8044 |  |  | AO-1 | AO | 1 | Condenser Water Pump-1 VFD Control | CP-01 | Condenser Pumps | VFD | Command
Panel-1 | DDC-03 | DDC-8044 |  |  | AO-2 | AO | 2 | Condenser Water Pump-2 VFD Control | CP-02 | Condenser Pumps | VFD | Command
Panel-1 | DDC-03 | DDC-8044 |  |  | AO-3 | AO | 3 | Condenser Water Pump-3 VFD Control | CP-03 | Condenser Pumps | VFD | Command
Panel-1 | DDC-03 | DDC-8044 |  |  | AO-4 | AO | 4 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-03 | DDC-8044 |  |  | DO-1 | DO | 1 | Condenser Water Pump-1 VFD On/Off Command | CP-01 | Condenser Pumps | Pump | Command
Panel-1 | DDC-03 | DDC-8044 |  |  | DO-2 | DO | 2 | Condenser Water Pump-2 VFD On/Off Command | CP-02 | Condenser Pumps | Pump | Command
Panel-1 | DDC-03 | DDC-8044 |  |  | DO-3 | DO | 3 | Condenser Water Pump-3 VFD On/Off Command | CP-03 | Condenser Pumps | Pump | Command
Panel-1 | DDC-03 | DDC-8044 |  |  | DO-4 | DO | 4 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-03 |  | Ext Module | IO-V0800 | DI-1 | DI | 9 | Condenser Water Pump-1 Trip Status | CP-01 | Condenser Pumps | Pump | Status
Panel-1 | DDC-03 |  | Ext Module | IO-V0800 | DI-2 | DI | 10 | Condenser Water Pump-2 Trip Status | CP-02 | Condenser Pumps | Pump | Status
Panel-1 | DDC-03 |  | Ext Module | IO-V0800 | DI-3 | DI | 11 | Condenser Water Pump-3 Trip Status | CP-03 | Condenser Pumps | Pump | Status
Panel-1 | DDC-03 |  | Ext Module | IO-V0800 | DI-4 | DI | 12 | Condenser Water Pump-1 Auto/Manual Status | CP-01 | Condenser Pumps | Pump | Status
Panel-1 | DDC-03 |  | Ext Module | IO-V0800 | DI-5 | DI | 13 | Condenser Water Pump-2 Auto/Manual Status | CP-02 | Condenser Pumps | Pump | Status
Panel-1 | DDC-03 |  | Ext Module | IO-V0800 | DI-6 | DI | 14 | Condenser Water Pump-3 Auto/Manual Status | CP-03 | Condenser Pumps | Pump | Status
Panel-1 | DDC-03 |  | Ext Module | IO-V0800 | DI-7 | DI | 15 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-03 |  | Ext Module | IO-V0800 | DI-8 | DI | 16 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-04 | DDC-8044 |  |  | UI-1 | AI | 1 | Cooling Tower-1 Fan-1 VFD Speed Feedback | CT-01-F-01 | Cooling Towers | VFD | Status
Panel-1 | DDC-04 | DDC-8044 |  |  | UI-2 | AI | 2 | Cooling Tower-1 Fan-2 VFD Speed Feedback | CT-01-F-02 | Cooling Towers | VFD | Status
Panel-1 | DDC-04 | DDC-8044 |  |  | UI-3 | AI | 3 | Cooling Tower-2 Fan-1 VFD Speed Feedback | CT-02-F-01 | Cooling Towers | VFD | Status
Panel-1 | DDC-04 | DDC-8044 |  |  | UI-4 | AI | 4 | Cooling Tower-2 Fan-2 VFD Speed Feedback | CT-02-F-02 | Cooling Towers | VFD | Status
Panel-1 | DDC-04 | DDC-8044 |  |  | UI-5 | AI | 5 | Cooling Tower-1 Sump Temperature-1 | CT-01-ST-01 | Cooling Towers | Sensor | Status
Panel-1 | DDC-04 | DDC-8044 |  |  | UI-6 | AI | 6 | Cooling Tower-1 Sump Temperature-2 | CT-01-ST-02 | Cooling Towers | Sensor | Status
Panel-1 | DDC-04 | DDC-8044 |  |  | UI-7 | AI | 7 | Cooling Tower-2 Sump Temperature-1 | CT-02-ST-01 | Cooling Towers | Sensor | Status
Panel-1 | DDC-04 | DDC-8044 |  |  | UI-8 | AI | 8 | Cooling Tower-2 Sump Temperature-2 | CT-02-ST-02 | Cooling Towers | Sensor | Status
Panel-1 | DDC-04 | DDC-8044 |  |  | AO-1 | AO | 1 | Cooling Tower-1 Fan-1 VFD Speed Control | CT-01-F-01 | Cooling Towers | VFD | Command
Panel-1 | DDC-04 | DDC-8044 |  |  | AO-2 | AO | 2 | Cooling Tower-1 Fan-2 VFD Speed Control | CT-01-F-02 | Cooling Towers | VFD | Command
Panel-1 | DDC-04 | DDC-8044 |  |  | AO-3 | AO | 3 | Cooling Tower-2 Fan-1 VFD Speed Control | CT-02-F-01 | Cooling Towers | VFD | Command
Panel-1 | DDC-04 | DDC-8044 |  |  | AO-4 | AO | 4 | Cooling Tower-2 Fan-2 VFD Speed Control | CT-02-F-02 | Cooling Towers | VFD | Command
Panel-1 | DDC-04 | DDC-8044 |  |  | DO-1 | DO | 1 | Cooling Tower-1 Fan-1 VFD On/Off Command | CT-01-F-01 | Cooling Towers | Cooling Tower | Command
Panel-1 | DDC-04 | DDC-8044 |  |  | DO-2 | DO | 2 | Cooling Tower-1 Fan-2 VFD On/Off Command | CT-01-F-02 | Cooling Towers | Cooling Tower | Command
Panel-1 | DDC-04 | DDC-8044 |  |  | DO-3 | DO | 3 | Cooling Tower-2 Fan-1 VFD On/Off Command | CT-02-F-01 | Cooling Towers | Cooling Tower | Command
Panel-1 | DDC-04 | DDC-8044 |  |  | DO-4 | DO | 4 | Cooling Tower-2 Fan-2 VFD On/Off Command | CT-02-F-02 | Cooling Towers | Cooling Tower | Command
Panel-1 | DDC-04 |  | Ext Module | IO-V0800 | DI-1 | DI | 9 | Cooling Tower-1 Fan-1 Run Status | CT-01-F-01 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | Ext Module | IO-V0800 | DI-2 | DI | 10 | Cooling Tower-1 Fan-2 Run Status | CT-01-F-02 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | Ext Module | IO-V0800 | DI-3 | DI | 11 | Cooling Tower-2 Fan-1 Run Status | CT-02-F-01 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | Ext Module | IO-V0800 | DI-4 | DI | 12 | Cooling Tower-2 Fan-2 Run Status | CT-02-F-02 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | Ext Module | IO-V0800 | DI-5 | DI | 13 | Cooling Tower-1 Level Switch (High) | CT-01-LS-01 | Cooling Towers | Sensor | Status
Panel-1 | DDC-04 |  | Ext Module | IO-V0800 | DI-6 | DI | 14 | Cooling Tower-1 Level Switch (Low) | CT-01-LS-02 | Cooling Towers | Sensor | Status
Panel-1 | DDC-04 |  | Ext Module | IO-V0800 | DI-7 | DI | 15 | Cooling Tower-2 Level Switch (High) | CT-02-LS-01 | Cooling Towers | Sensor | Status
Panel-1 | DDC-04 |  | Ext Module | IO-V0800 | DI-8 | DI | 16 | Cooling Tower-2 Level Switch (Low) | CT-02-LS-02 | Cooling Towers | Sensor | Status
Panel-1 | DDC-04 |  | IO Module-01 | IO-0800-485 | DI-1 | DI | 1 | Cooling Tower-1 Fan-1 Auto/Manual Status | CT-01-F-01 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | IO Module-01 | IO-0800-485 | DI-2 | DI | 2 | Cooling Tower-1 Fan-2 Auto/Manual Status | CT-01-F-02 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | IO Module-01 | IO-0800-485 | DI-3 | DI | 3 | Cooling Tower-2 Fan-1 Auto/Manual Status | CT-02-F-01 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | IO Module-01 | IO-0800-485 | DI-4 | DI | 4 | Cooling Tower-2 Fan-2 Auto/Manual Status | CT-02-F-02 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | IO Module-01 | IO-0800-485 | DI-5 | DI | 5 | Cooling Tower-1 Fan-1 Trip Status | CT-01-F-01 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | IO Module-01 | IO-0800-485 | DI-6 | DI | 6 | Cooling Tower-1 Fan-2 Trip Status | CT-01-F-02 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | IO Module-01 | IO-0800-485 | DI-7 | DI | 7 | Cooling Tower-2 Fan-1 Trip Status | CT-02-F-01 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | IO Module-01 | IO-0800-485 | DI-8 | DI | 8 | Cooling Tower-2 Fan-2 Trip Status | CT-02-F-02 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-04 |  | IO Module-02 | IO-0800-485 | DI-1 | DI | 1 | Cooling Tower-1 Inlet-1 isolation valves Open/Close Status | CT-01-VLV-01 | Cooling Towers | Valve | Status
Panel-1 | DDC-04 |  | IO Module-02 | IO-0800-485 | DI-2 | DI | 2 | Cooling Tower-1 Inlet-2 isolation valves Open/Close Status | CT-01-VLV-02 | Cooling Towers | Valve | Status
Panel-1 | DDC-04 |  | IO Module-02 | IO-0800-485 | DI-3 | DI | 3 | Cooling Tower-1 Outlet-1 isolation valves Open/Close Status | CT-01-VLV-03 | Cooling Towers | Valve | Status
Panel-1 | DDC-04 |  | IO Module-02 | IO-0800-485 | DI-4 | DI | 4 | Cooling Tower-1 Outlet-2 isolation valves Open/Close Status | CT-01-VLV-04 | Cooling Towers | Valve | Status
Panel-1 | DDC-04 |  | IO Module-02 | IO-0800-485 | DI-5 | DI | 5 | Cooling Tower-2 Inlet-1 isolation valves Open/Close Status | CT-02-VLV-01 | Cooling Towers | Valve | Status
Panel-1 | DDC-04 |  | IO Module-02 | IO-0800-485 | DI-6 | DI | 6 | Cooling Tower-2 Intlet-2 isolation valves Open/Close Status | CT-02-VLV-02 | Cooling Towers | Valve | Status
Panel-1 | DDC-04 |  | IO Module-02 | IO-0800-485 | DI-7 | DI | 7 | Cooling Tower-2 Outlet-1 isolation valves Open/Close Status | CT-02-VLV-03 | Cooling Towers | Valve | Status
Panel-1 | DDC-04 |  | IO Module-02 | IO-0800-485 | DI-8 | DI | 8 | Cooling Tower-2 Outlet-2 isolation valves Open/Close Status | CT-02-VLV-04 | Cooling Towers | Valve | Status
Panel-1 | DDC-04 |  | IO Module-03 | IO-0008-485 | DO-1 | DO | 1 | Cooling Tower-1 Inlet-1 isolation valves Open/Close Command | CT-01-VLV-01 | Cooling Towers | Valve | Command
Panel-1 | DDC-04 |  | IO Module-03 | IO-0008-485 | DO-2 | DO | 2 | Cooling Tower-1 Inlet-2 isolation valves Open/Close Command | CT-01-VLV-02 | Cooling Towers | Valve | Command
Panel-1 | DDC-04 |  | IO Module-03 | IO-0008-485 | DO-3 | DO | 3 | Cooling Tower-1 Outlet-1 isolation valves Open/Close Command | CT-01-VLV-03 | Cooling Towers | Valve | Command
Panel-1 | DDC-04 |  | IO Module-03 | IO-0008-485 | DO-4 | DO | 4 | Cooling Tower-1 Outlet-2 isolation valves Open/Close Command | CT-01-VLV-04 | Cooling Towers | Valve | Command
Panel-1 | DDC-04 |  | IO Module-03 | IO-0008-485 | DO-5 | DO | 5 | Cooling Tower-2 Inlet-1 isolation valves Open/Close Command | CT-02-VLV-01 | Cooling Towers | Valve | Command
Panel-1 | DDC-04 |  | IO Module-03 | IO-0008-485 | DO-6 | DO | 6 | Cooling Tower-2 Intlet-2 isolation valves Open/Close Command | CT-02-VLV-02 | Cooling Towers | Valve | Command
Panel-1 | DDC-04 |  | IO Module-03 | IO-0008-485 | DO-7 | DO | 7 | Cooling Tower-2 Outlet-1 isolation valves Open/Close Command | CT-02-VLV-03 | Cooling Towers | Valve | Command
Panel-1 | DDC-04 |  | IO Module-03 | IO-0008-485 | DO-8 | DO | 8 | Cooling Tower-2 Outlet-2 isolation valves Open/Close Command | CT-02-VLV-04 | Cooling Towers | Valve | Command
Panel-1 | DDC-05 | DDC-8044 |  |  | UI-1 | AI | 1 | Cooling Tower-3 Fan-1 VFD Speed Feedback | CT-03-F-01 | Cooling Towers | VFD | Status
Panel-1 | DDC-05 | DDC-8044 |  |  | UI-2 | AI | 2 | Cooling Tower-3 Fan-2 VFD Speed Feedback | CT-03-F-02 | Cooling Towers | VFD | Status
Panel-1 | DDC-05 | DDC-8044 |  |  | UI-3 | AI | 3 | Cooling Tower-3 Sump Temperature-1 | CT-03-ST-01 | Cooling Towers | Sensor | Status
Panel-1 | DDC-05 | DDC-8044 |  |  | UI-4 | AI | 4 | Cooling Tower-3 Sump Temperature-2 | CT-03-ST-02 | Cooling Towers | Sensor | Status
Panel-1 | DDC-05 | DDC-8044 |  |  | UI-5 | DI | 5 | Cooling Tower-3 Fan-1 Run Status | CT-03-F-01 | Cooling Towers | VFD | Status
Panel-1 | DDC-05 | DDC-8044 |  |  | UI-6 | DI | 6 | Cooling Tower-3 Fan-2 Run Status | CT-03-F-02 | Cooling Towers | VFD | Status
Panel-1 | DDC-05 | DDC-8044 |  |  | UI-7 | DI | 7 | Cooling Tower-3 Outlet-1 isolation valves Open/Close Status | CT-03-VLV-03 | Cooling Towers | Valve | Status
Panel-1 | DDC-05 | DDC-8044 |  |  | UI-8 | DI | 8 | Cooling Tower-3 Outtlet-2 isolation valves Open/Close Status | CT-03-VLV-04 | Cooling Towers | Valve | Status
Panel-1 | DDC-05 | DDC-8044 |  |  | AO-1 | AO | 1 | Cooling Tower-3 Fan-1 VFD Speed Control | CT-03-F-01 | Cooling Towers | VFD | Command
Panel-1 | DDC-05 | DDC-8044 |  |  | AO-2 | AO | 2 | Cooling Tower-3 Fan-2 VFD Speed Control | CT-03-F-02 | Cooling Towers | VFD | Command
Panel-1 | DDC-05 | DDC-8044 |  |  | AO-3 | AO | 3 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-05 | DDC-8044 |  |  | AO-4 | AO | 4 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-05 | DDC-8044 |  |  | DO-1 | DO | 1 | Cooling Tower-3 Fan-1 VFD On/Off Command | CT-03-F-01 | Cooling Towers | Cooling Tower | Command
Panel-1 | DDC-05 | DDC-8044 |  |  | DO-2 | DO | 2 | Cooling Tower-3 Fan-2 VFD On/Off Command | CT-03-F-02 | Cooling Towers | Cooling Tower | Command
Panel-1 | DDC-05 | DDC-8044 |  |  | DO-3 | DO | 3 | Cooling Tower-3 Outlet-1 isolation valves Open/Close Command | CT-03-VLV-03 | Cooling Towers | Valve | Command
Panel-1 | DDC-05 | DDC-8044 |  |  | DO-4 | DO | 4 | Cooling Tower-3 Outlet-2 isolation valves Open/Close Command | CT-03-VLV-04 | Cooling Towers | Valve | Command
Panel-1 | DDC-05 |  | Ext Module | IO-V6002 | UI-1 | DI | 9 | Cooling Tower-3 Fan-1 Auto.Manual Status | CT-03-F-01 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-05 |  | Ext Module | IO-V6002 | UI-2 | DI | 10 | Cooling Tower-3 Fan-2 Auto.Manual Status | CT-03-F-02 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-05 |  | Ext Module | IO-V6002 | UI-3 | DI | 11 | Cooling Tower-3 Fan-1 Trip Status | CT-03-F-01 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-05 |  | Ext Module | IO-V6002 | UI-4 | DI | 12 | Cooling Tower-3 Fan-2 Trip Status | CT-03-F-02 | Cooling Towers | Cooling Tower | Status
Panel-1 | DDC-05 |  | Ext Module | IO-V6002 | UI-5 | DI | 13 | Cooling Tower-3 Level Switch (High) | CT-03-LS-01 | Cooling Towers | Sensor | Status
Panel-1 | DDC-05 |  | Ext Module | IO-V6002 | UI-6 | DI | 14 | Cooling Tower-3 Level Switch (Low) | CT-03-LS-02 | Cooling Towers | Sensor | Status
Panel-1 | DDC-05 |  | Ext Module | IO-V6002 | DO-1 | DO | 5 | Cooling Tower-3 Inlet-1 isolation valves Open/Close Command | CT-03-VLV-01 | Cooling Towers | Valve | Command
Panel-1 | DDC-05 |  | Ext Module | IO-V6002 | DO-2 | DO | 6 | Cooling Tower-3 Intlet-2 isolation valves Open/Close Command | CT-03-VLV-02 | Cooling Towers | Valve | Command
Panel-1 | DDC-05 |  | IO Module-01 | IO-0800-485 | DI-1 | DI | 1 | Cooling Tower-3 Inlet-1 isolation valves Open/Close Status | CT-03-VLV-01 | Cooling Towers | Valve | Status
Panel-1 | DDC-05 |  | IO Module-01 | IO-0800-485 | DI-2 | DI | 2 | Cooling Tower-3 Intlet-2 isolation valves Open/Close Status | CT-03-VLV-02 | Cooling Towers | Valve | Status
Panel-1 | DDC-05 |  | IO Module-01 | IO-0800-485 | DI-3 | DI | 3 | Cooling Tower-4 Level Switch (High) |  | Spare | Sensor | Status
Panel-1 | DDC-05 |  | IO Module-01 | IO-0800-485 | DI-4 | DI | 4 | Cooling Tower-4 Level Switch (Low) |  | Spare | Sensor | Status
Panel-1 | DDC-05 |  | IO Module-01 | IO-0800-485 | DI-5 | DI | 5 | Cooling Tower-5 Level Switch (High) |  | Spare | Sensor | Status
Panel-1 | DDC-05 |  | IO Module-01 | IO-0800-485 | DI-6 | DI | 6 | Cooling Tower-5 Level Switch (Low) |  | Spare | Sensor | Status
Panel-1 | DDC-05 |  | IO Module-01 | IO-0800-485 | DI-7 | DI | 7 | Cooling Tower-6 Level Switch (High) |  | Spare | Sensor | Status
Panel-1 | DDC-05 |  | IO Module-01 | IO-0800-485 | DI-8 | DI | 8 | Cooling Tower-6 Level Switch (Low) |  | Spare | Sensor | Status
Panel-1 | DDC-06 | DDC-8044 |  |  | UI-1 | DI | 1 | Exhaust Fan-1 Run Status | EX-01 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 | DDC-8044 |  |  | UI-2 | DI | 2 | Exhaust Fan-2 Run Status | EX-02 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 | DDC-8044 |  |  | UI-3 | DI | 3 | Exhaust Fan-3 Run Status | EX-03 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 | DDC-8044 |  |  | UI-4 | DI | 4 | Exhaust Fan-4 Run Status | EX-04 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 | DDC-8044 |  |  | UI-5 | DI | 5 | Exhaust Fan-1 Trip Status | EX-01 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 | DDC-8044 |  |  | UI-6 | DI | 6 | Exhaust Fan-2 Trip Status | EX-02 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 | DDC-8044 |  |  | UI-7 | DI | 7 | Exhaust Fan-3 Trip Status | EX-03 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 | DDC-8044 |  |  | UI-8 | DI | 8 | Exhaust Fan-4 Trip Status | EX-04 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 | DDC-8044 |  |  | AO-1 | AO | 1 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-06 | DDC-8044 |  |  | AO-2 | AO | 2 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-06 | DDC-8044 |  |  | AO-3 | AO | 3 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-06 | DDC-8044 |  |  | AO-4 | AO | 4 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-06 | DDC-8044 |  |  | DO-1 | DO | 1 | Exhaust Fan-1 On/Off Command | EX-01 | Exhaust Fans | Exhaust Fan | Command
Panel-1 | DDC-06 | DDC-8044 |  |  | DO-2 | DO | 2 | Exhaust Fan-2 On/Off Command | EX-02 | Exhaust Fans | Exhaust Fan | Command
Panel-1 | DDC-06 | DDC-8044 |  |  | DO-3 | DO | 3 | Exhaust Fan-3 On/Off Command | EX-03 | Exhaust Fans | Exhaust Fan | Command
Panel-1 | DDC-06 | DDC-8044 |  |  | DO-4 | DO | 4 | Exhaust Fan-4 On/Off Command | EX-04 | Exhaust Fans | Exhaust Fan | Command
Panel-1 | DDC-06 |  | Ext Module | IO-V6002 | UI-1 | DI | 9 | Exhaust Fan-1 Auto/Manual Status | EX-01 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 |  | Ext Module | IO-V6002 | UI-2 | DI | 10 | Exhaust Fan-2 Auto/Manual Status | EX-02 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 |  | Ext Module | IO-V6002 | UI-3 | DI | 11 | Exhaust Fan-3 Auto/Manual Status | EX-03 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 |  | Ext Module | IO-V6002 | UI-4 | DI | 12 | Exhaust Fan-4 Auto/Manual Status | EX-04 | Exhaust Fans | Exhaust Fan | Status
Panel-1 | DDC-06 |  | Ext Module | IO-V6002 | UI-5 | DI | 13 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-06 |  | Ext Module | IO-V6002 | UI-6 | DI | 14 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-06 |  | Ext Module | IO-V6002 | DO-1 | DO | 5 | Spare |  | Spare | Spare | Spare
Panel-1 | DDC-06 |  | Ext Module | IO-V6002 | DO-2 | DO | 6 | Spare |  | Spare | Spare | Spare

## Name_Handler
DDC ID | Object type | Instance Id | short name | Description | Point Type | GL | DDC No | 00 | Device No | Equipment Type | Param Type | Parameter No | GL CODE | Index | Equipment Name
DDC01 | analogInput | 1 | par_out_air_temp_00 | Outside Air Temp monitoring | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 001 | GL 01 00 01 C0 0 001 | 1 | Header
DDC01 | analogOutput | 1 | cmd_bypass_vlv_00 | Bypass Modulating Valve Control | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 009 | GL 01 00 01 C0 0 009 | 9 | Header
DDC01 | analogInput | 2 | par_out_air_humidity_00 | Outside Air Relative Humidity Monitoring | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 002 | GL 01 00 01 C0 0 002 | 2 | Header
DDC01 | analogInput | 3 | par_cwh_sup_temp_00 | CHW Common Supply Header Temperature | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 003 | GL 01 00 01 C0 0 003 | 3 | Header
DDC01 | analogInput | 4 | par_cwh_ret_temp_00 | CHW Common Return Header Temperature | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 004 | GL 01 00 01 C0 0 004 | 4 | Header
DDC01 | analogInput | 5 | par_cdw_sup_temp_00 | Condenser Water Supply Header Temperature | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 005 | GL 01 00 01 C0 0 005 | 5 | Header
DDC01 | binaryOutput | 5 | cmd_on_off_00 | Chiller-1 Enable/Disable Command | Hardpoint | GL | 01 | 00 | 01 | B0 | 0 | 002 | GL 01 00 01 B0 0 002 | 2 | Chiller
DDC01 | analogInput | 6 | par_cdw_ret_temp_00 | Condenser Water Return Header Temperature | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 006 | GL 01 00 01 C0 0 006 | 6 | Header
DDC01 | analogInput | 7 | par_bypass_temp_00 | Bypass Temperature | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 007 | GL 01 00 01 C0 0 007 | 7 | Header
DDC01 | analogInput | 8 | sts_bypass_vlv_00 | Bypass Modulating Valve Feedback | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 008 | GL 01 00 01 C0 0 008 | 8 | Header
DDC01 | analogInput | 9 | par_cdw_sup_flow_00 | CDW Common supply header flow | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 00A | GL 01 00 01 C0 0 00A | 10 | Header
DDC01 | binaryInput | 9 | sts_on_off_00 | Chiller-1 Run Status | Hardpoint | GL | 01 | 00 | 01 | B0 | 0 | 001 | GL 01 00 01 B0 0 001 | 1 | Chiller
DDC01 | analogInput | 10 | par_cwh_sup_ret_pressure_00 | CHW Common Supply and Return Header Pressure monitoring | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 00B | GL 01 00 01 C0 0 00B | 11 | Header
DDC01 | analogInput | 11 | par_dpt_01 | Diff Pressure Monitoring @Main Header | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 00C | GL 01 00 01 C0 0 00C | 12 | Header
DDC01 | analogInput | 12 | par_dpt_02 | Diff Pressure Monitoring @AHU Header | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 00D | GL 01 00 01 C0 0 00D | 13 | Header
DDC01 | analogInput | 13 | par_decimal_meter_00 | Decimal Meter | Hardpoint | GL | 01 | 00 | 01 | C0 | 0 | 00E | GL 01 00 01 C0 0 00E | 14 | Header
DDC01_01 | binaryInput | 1 | sts_auto_manual_00 | Chiller-1 Auto/Manual Status | Hardpoint | GL | 01 | 00 | 01 | B0 | 0 | 003 | GL 01 00 01 B0 0 003 | 3 | Chiller
DDC01_01 | binaryInput | 2 | sts_auto_manual_00 | Chiller-2 Auto/Manual Status | Hardpoint | GL | 01 | 00 | 02 | B0 | 0 | 003 | GL 01 00 02 B0 0 003 | 3 | Chiller
DDC01_01 | binaryInput | 3 | sts_auto_manual_00 | Chiller-3 Auto/Manual Status | Hardpoint | GL | 01 | 00 | 03 | B0 | 0 | 003 | GL 01 00 03 B0 0 003 | 3 | Chiller
DDC01_01 | binaryInput | 4 | alm_trip_00 | Chiller-1 Fault/Alarm Status | Hardpoint | GL | 01 | 00 | 01 | B0 | A | 004 | GL 01 00 01 B0 A 004 | 4 | Chiller
DDC01_01 | binaryInput | 5 | alm_trip_00 | Chiller-2 Fault/Alarm Status | Hardpoint | GL | 01 | 00 | 02 | B0 | A | 004 | GL 01 00 02 B0 A 004 | 4 | Chiller
DDC01_01 | binaryInput | 6 | alm_trip_00 | Chiller-3 Fault/Alarm Status | Hardpoint | GL | 01 | 00 | 03 | B0 | A | 004 | GL 01 00 03 B0 A 004 | 4 | Chiller
DDC01_02 | binaryInput | 1 | sts_evap_vlv_on_off_00 | Chiller-1 Motorized Valve-1 Feedback | Hardpoint | GL | 01 | 00 | 01 | B0 | 0 | 005 | GL 01 00 01 B0 0 005 | 5 | Chiller
DDC01_02 | binaryInput | 2 | sts_cond_vlv_on_off_00 | Chiller-1 Motorized Valve-2 Feedback | Hardpoint | GL | 01 | 00 | 01 | B0 | 0 | 006 | GL 01 00 01 B0 0 006 | 6 | Chiller
DDC01_02 | binaryInput | 3 | sts_evap_vlv_on_off_00 | Chiller-2 Motorized Valve-1 Feedback | Hardpoint | GL | 01 | 00 | 02 | B0 | 0 | 005 | GL 01 00 02 B0 0 005 | 5 | Chiller
DDC01_02 | binaryInput | 4 | sts_cond_vlv_on_off_00 | Chiller-2 Motorized Valve-2 Feedback | Hardpoint | GL | 01 | 00 | 02 | B0 | 0 | 006 | GL 01 00 02 B0 0 006 | 6 | Chiller
DDC01_02 | binaryInput | 5 | sts_evap_vlv_on_off_00 | Chiller-3 Motorized Valve-1 Feedback | Hardpoint | GL | 01 | 00 | 03 | B0 | 0 | 005 | GL 01 00 03 B0 0 005 | 5 | Chiller
DDC01_02 | binaryInput | 6 | sts_cond_vlv_on_off_00 | Chiller-3 Motorized Valve-2 Feedback | Hardpoint | GL | 01 | 00 | 03 | B0 | 0 | 006 | GL 01 00 03 B0 0 006 | 6 | Chiller
DDC01_02 | binaryInput | 7 | sts_on_off_00 | Chiller-2 Run Status | Hardpoint | GL | 01 | 00 | 02 | B0 | 0 | 001 | GL 01 00 02 B0 0 001 | 1 | Chiller
DDC01_02 | binaryInput | 8 | sts_on_off_00 | Chiller-3 Run Status | Hardpoint | GL | 01 | 00 | 03 | B0 | 0 | 001 | GL 01 00 03 B0 0 001 | 1 | Chiller
DDC01_03 | binaryOutput | 1 | cmd_evap_vlv_on_off_00 | Chiller-1 Motorized Valve-1 Command | Hardpoint | GL | 01 | 00 | 01 | B0 | 0 | 007 | GL 01 00 01 B0 0 007 | 7 | Chiller
DDC01_03 | binaryOutput | 2 | cmd_cond_vlv_on_off_00 | Chiller-1 Motorized Valve-2 Command | Hardpoint | GL | 01 | 00 | 01 | B0 | 0 | 008 | GL 01 00 01 B0 0 008 | 8 | Chiller
DDC01_03 | binaryOutput | 3 | cmd_evap_vlv_on_off_00 | Chiller-2 Motorized Valve-1 Command | Hardpoint | GL | 01 | 00 | 02 | B0 | 0 | 007 | GL 01 00 02 B0 0 007 | 7 | Chiller
DDC01_03 | binaryOutput | 4 | cmd_cond_vlv_on_off_00 | Chiller-2 Motorized Valve-2 Command | Hardpoint | GL | 01 | 00 | 02 | B0 | 0 | 008 | GL 01 00 02 B0 0 008 | 8 | Chiller
DDC01_03 | binaryOutput | 5 | cmd_evap_vlv_on_off_00 | Chiller-3 Motorized Valve-1 Command | Hardpoint | GL | 01 | 00 | 03 | B0 | 0 | 007 | GL 01 00 03 B0 0 007 | 7 | Chiller
DDC01_03 | binaryOutput | 6 | cmd_cond_vlv_on_off_00 | Chiller-3 Motorized Valve-2 Command | Hardpoint | GL | 01 | 00 | 03 | B0 | 0 | 008 | GL 01 00 03 B0 0 008 | 8 | Chiller
DDC01_03 | binaryOutput | 7 | cmd_on_off_00 | Chiller-2 Enable/Disable Command | Hardpoint | GL | 01 | 00 | 02 | B0 | 0 | 002 | GL 01 00 02 B0 0 002 | 2 | Chiller
DDC01_03 | binaryOutput | 8 | cmd_on_off_00 | Chiller-3 Enable/Disable Command | Hardpoint | GL | 01 | 00 | 03 | B0 | 0 | 002 | GL 01 00 03 B0 0 002 | 2 | Chiller
DDC02 | analogInput | 1 | sts_pump_vfd_frequency_00 | Chilled Water Pump-1 VFD Feedback | Hardpoint | GL | 02 | 00 | 01 | B2 | 0 | 004 | GL 02 00 01 B2 0 004 | 4 | Primary Variable pump
DDC02 | analogOutput | 1 | cmd_pump_vfd_frequency_00 | Chilled Water Pump-1 VFD Control | Hardpoint | GL | 02 | 00 | 01 | B2 | 0 | 005 | GL 02 00 01 B2 0 005 | 5 | Primary Variable pump
DDC02 | binaryOutput | 1 | cmd_on_off_00 | Chilled Water Pump-1 VFD On/Off Command | Hardpoint | GL | 02 | 00 | 01 | B2 | 0 | 006 | GL 02 00 01 B2 0 006 | 6 | Primary Variable pump
DDC02 | analogInput | 2 | sts_pump_vfd_frequency_00 | Chilled Water Pump-2 VFD Feedback | Hardpoint | GL | 02 | 00 | 02 | B2 | 0 | 004 | GL 02 00 02 B2 0 004 | 4 | Primary Variable pump
DDC02 | analogOutput | 2 | cmd_pump_vfd_frequency_00 | Chilled Water Pump-2 VFD Control | Hardpoint | GL | 02 | 00 | 02 | B2 | 0 | 005 | GL 02 00 02 B2 0 005 | 5 | Primary Variable pump
DDC02 | binaryOutput | 2 | cmd_on_off_00 | Chilled Water Pump-2 VFD On/Off Command | Hardpoint | GL | 02 | 00 | 02 | B2 | 0 | 006 | GL 02 00 02 B2 0 006 | 6 | Primary Variable pump
DDC02 | analogInput | 3 | sts_pump_vfd_frequency_00 | Chilled Water Pump-3 VFD Feedback | Hardpoint | GL | 02 | 00 | 03 | B2 | 0 | 004 | GL 02 00 03 B2 0 004 | 4 | Primary Variable pump
DDC02 | analogOutput | 3 | cmd_pump_vfd_frequency_00 | Chilled Water Pump-3 VFD Control | Hardpoint | GL | 02 | 00 | 03 | B2 | 0 | 005 | GL 02 00 03 B2 0 005 | 5 | Primary Variable pump
DDC02 | binaryOutput | 3 | cmd_on_off_00 | Chilled Water Pump-3 VFD On/Off Command | Hardpoint | GL | 02 | 00 | 03 | B2 | 0 | 006 | GL 02 00 03 B2 0 006 | 6 | Primary Variable pump
DDC02 | binaryInput | 4 | sts_on_off_00 | Chilled Water Pump-1 run Status | Hardpoint | GL | 02 | 00 | 01 | B2 | 0 | 001 | GL 02 00 01 B2 0 001 | 1 | Primary Variable pump
DDC02 | binaryInput | 5 | sts_on_off_00 | Chilled Water Pump-2 run Status | Hardpoint | GL | 02 | 00 | 02 | B2 | 0 | 001 | GL 02 00 02 B2 0 001 | 1 | Primary Variable pump
DDC02 | binaryInput | 6 | sts_on_off_00 | Chilled Water Pump-3 run Status | Hardpoint | GL | 02 | 00 | 03 | B2 | 0 | 001 | GL 02 00 03 B2 0 001 | 1 | Primary Variable pump
DDC02 | binaryInput | 9 | alm_trip_00 | Chilled Water Pump-1 Trip Status | Hardpoint | GL | 02 | 00 | 01 | B2 | A | 003 | GL 02 00 01 B2 A 003 | 3 | Primary Variable pump
DDC02 | binaryInput | 10 | alm_trip_00 | Chilled Water Pump-2 Trip Status | Hardpoint | GL | 02 | 00 | 02 | B2 | A | 003 | GL 02 00 02 B2 A 003 | 3 | Primary Variable pump
DDC02 | binaryInput | 11 | alm_trip_00 | Chilled Water Pump-3 Trip Status | Hardpoint | GL | 02 | 00 | 03 | B2 | A | 003 | GL 02 00 03 B2 A 003 | 3 | Primary Variable pump
DDC02 | binaryInput | 12 | sts_auto_manual_00 | Chilled Water Pump-1 Auto/Manual Status | Hardpoint | GL | 02 | 00 | 01 | B2 | 0 | 002 | GL 02 00 01 B2 0 002 | 2 | Primary Variable pump
DDC02 | binaryInput | 13 | sts_auto_manual_00 | Chilled Water Pump-2 Auto/Manual Status | Hardpoint | GL | 02 | 00 | 02 | B2 | 0 | 002 | GL 02 00 02 B2 0 002 | 2 | Primary Variable pump
DDC02 | binaryInput | 14 | sts_auto_manual_00 | Chilled Water Pump-3 Auto/Manual Status | Hardpoint | GL | 02 | 00 | 03 | B2 | 0 | 002 | GL 02 00 03 B2 0 002 | 2 | Primary Variable pump
DDC03 | analogInput | 1 | sts_pump_vfd_frequency_00 | Condenser Water Pump-1 VFD Feedback | Hardpoint | GL | 03 | 00 | 01 | B4 | 0 | 004 | GL 03 00 01 B4 0 004 | 4 | Condenser pump
DDC03 | analogOutput | 1 | cmd_pump_vfd_frequency_00 | Condenser Water Pump-1 VFD Control | Hardpoint | GL | 03 | 00 | 01 | B4 | 0 | 005 | GL 03 00 01 B4 0 005 | 5 | Condenser pump
DDC03 | binaryOutput | 1 | cmd_on_off_00 | Condenser Water Pump-1 VFD On/Off Command | Hardpoint | GL | 03 | 00 | 01 | B4 | 0 | 006 | GL 03 00 01 B4 0 006 | 6 | Condenser pump
DDC03 | analogInput | 2 | sts_pump_vfd_frequency_00 | Condenser Water Pump-2 VFD Feedback | Hardpoint | GL | 03 | 00 | 02 | B4 | 0 | 004 | GL 03 00 02 B4 0 004 | 4 | Condenser pump
DDC03 | analogOutput | 2 | cmd_pump_vfd_frequency_00 | Condenser Water Pump-2 VFD Control | Hardpoint | GL | 03 | 00 | 02 | B4 | 0 | 005 | GL 03 00 02 B4 0 005 | 5 | Condenser pump
DDC03 | binaryOutput | 2 | cmd_on_off_00 | Condenser Water Pump-2 VFD On/Off Command | Hardpoint | GL | 03 | 00 | 02 | B4 | 0 | 006 | GL 03 00 02 B4 0 006 | 6 | Condenser pump
DDC03 | analogInput | 3 | sts_pump_vfd_frequency_00 | Condenser Water Pump-3 VFD Feedback | Hardpoint | GL | 03 | 00 | 03 | B4 | 0 | 004 | GL 03 00 03 B4 0 004 | 4 | Condenser pump
DDC03 | analogOutput | 3 | cmd_pump_vfd_frequency_00 | Condenser Water Pump-3 VFD Control | Hardpoint | GL | 03 | 00 | 03 | B4 | 0 | 005 | GL 03 00 03 B4 0 005 | 5 | Condenser pump
DDC03 | binaryOutput | 3 | cmd_on_off_00 | Condenser Water Pump-3 VFD On/Off Command | Hardpoint | GL | 03 | 00 | 03 | B4 | 0 | 006 | GL 03 00 03 B4 0 006 | 6 | Condenser pump
DDC03 | binaryInput | 4 | sts_on_off_00 | Condenser Water Pump-1 run Status | Hardpoint | GL | 03 | 00 | 01 | B4 | 0 | 001 | GL 03 00 01 B4 0 001 | 1 | Condenser pump
DDC03 | binaryInput | 5 | sts_on_off_00 | Condenser Water Pump-2 run Status | Hardpoint | GL | 03 | 00 | 02 | B4 | 0 | 001 | GL 03 00 02 B4 0 001 | 1 | Condenser pump
DDC03 | binaryInput | 6 | sts_on_off_00 | Condenser Water Pump-3 run Status | Hardpoint | GL | 03 | 00 | 03 | B4 | 0 | 001 | GL 03 00 03 B4 0 001 | 1 | Condenser pump
DDC03 | binaryInput | 9 | alm_trip_00 | Condenser Water Pump-1 Trip Status | Hardpoint | GL | 03 | 00 | 01 | B4 | A | 003 | GL 03 00 01 B4 A 003 | 3 | Condenser pump
DDC03 | binaryInput | 10 | alm_trip_00 | Condenser Water Pump-2 Trip Status | Hardpoint | GL | 03 | 00 | 02 | B4 | A | 003 | GL 03 00 02 B4 A 003 | 3 | Condenser pump
DDC03 | binaryInput | 11 | alm_trip_00 | Condenser Water Pump-3 Trip Status | Hardpoint | GL | 03 | 00 | 03 | B4 | A | 003 | GL 03 00 03 B4 A 003 | 3 | Condenser pump
DDC03 | binaryInput | 12 | sts_auto_manual_00 | Condenser Water Pump-1 Auto/Manual Status | Hardpoint | GL | 03 | 00 | 01 | B4 | 0 | 002 | GL 03 00 01 B4 0 002 | 2 | Condenser pump
DDC03 | binaryInput | 13 | sts_auto_manual_00 | Condenser Water Pump-2 Auto/Manual Status | Hardpoint | GL | 03 | 00 | 02 | B4 | 0 | 002 | GL 03 00 02 B4 0 002 | 2 | Condenser pump
DDC03 | binaryInput | 14 | sts_auto_manual_00 | Condenser Water Pump-3 Auto/Manual Status | Hardpoint | GL | 03 | 00 | 03 | B4 | 0 | 002 | GL 03 00 03 B4 0 002 | 2 | Condenser pump
DDC04 | analogInput | 1 | sts_fan_vfd_frequency_01 | Cooling Tower-1 Fan-1 VFD Speed Feedback | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 001 | GL 04 00 01 B7 0 001 | 1 | Cooling Tower
DDC04 | analogOutput | 1 | cmd_fan_vfd_frequency_01 | Cooling Tower-1 Fan-1 VFD Speed Control | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 002 | GL 04 00 01 B7 0 002 | 2 | Cooling Tower
DDC04 | binaryOutput | 1 | cmd_fan_on_off_01 | Cooling Tower-1 Fan-1 VFD On/Off Command | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 003 | GL 04 00 01 B7 0 003 | 3 | Cooling Tower
DDC04 | analogInput | 2 | sts_fan_vfd_frequency_02 | Cooling Tower-2 Fan-1 VFD Speed Feedback | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 004 | GL 04 00 01 B7 0 004 | 4 | Cooling Tower
DDC04 | analogOutput | 2 | cmd_fan_vfd_frequency_02 | Cooling Tower-2 Fan-1 VFD Speed Control | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 005 | GL 04 00 01 B7 0 005 | 5 | Cooling Tower
DDC04 | binaryOutput | 2 | cmd_fan_on_off_02 | Cooling Tower-2 Fan-1 VFD On/Off Command | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 006 | GL 04 00 01 B7 0 006 | 6 | Cooling Tower
DDC04 | analogInput | 3 | sts_fan_vfd_frequency_01 | Cooling Tower-3 Fan-1 VFD Speed Feedback | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 001 | GL 04 00 02 B7 0 001 | 1 | Cooling Tower
DDC04 | analogOutput | 3 | cmd_fan_vfd_frequency_01 | Cooling Tower-3 Fan-1 VFD Speed Control | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 002 | GL 04 00 02 B7 0 002 | 2 | Cooling Tower
DDC04 | binaryOutput | 3 | cmd_fan_on_off_01 | Cooling Tower-3 Fan-1 VFD On/Off Command | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 003 | GL 04 00 02 B7 0 003 | 3 | Cooling Tower
DDC04 | analogInput | 4 | sts_fan_vfd_frequency_02 | Cooling Tower-4 Fan-1 VFD Speed Feedback | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 004 | GL 04 00 02 B7 0 004 | 4 | Cooling Tower
DDC04 | analogOutput | 4 | cmd_fan_vfd_frequency_02 | Cooling Tower-4 Fan-1 VFD Speed Control | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 005 | GL 04 00 02 B7 0 005 | 5 | Cooling Tower
DDC04 | binaryOutput | 4 | cmd_fan_on_off_02 | Cooling Tower-4 Fan-1 VFD On/Off Command | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 006 | GL 04 00 02 B7 0 006 | 6 | Cooling Tower
DDC04 | analogInput | 5 | par_sump_temp_01 | Cooling Tower-1 Sump Temperature-1 | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 007 | GL 04 00 01 B7 0 007 | 7 | Cooling Tower
DDC04 | analogInput | 6 | par_sump_temp_02 | Cooling Tower-2 Sump Temperature-1 | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 008 | GL 04 00 01 B7 0 008 | 8 | Cooling Tower
DDC04 | analogInput | 7 | par_sump_temp_01 | Cooling Tower-3 Sump Temperature-1 | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 007 | GL 04 00 02 B7 0 007 | 7 | Cooling Tower
DDC04 | analogInput | 8 | par_sump_temp_02 | Cooling Tower-4 Sump Temperature-1 | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 008 | GL 04 00 02 B7 0 008 | 8 | Cooling Tower
DDC04 | binaryInput | 9 | sts_fan_on_off_01 | Cooling Tower-1 Fan-1 Run Status | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 009 | GL 04 00 01 B7 0 009 | 9 | Cooling Tower
DDC04 | binaryInput | 10 | sts_fan_on_off_02 | Cooling Tower-2 Fan-1 Run Status | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 00A | GL 04 00 01 B7 0 00A | 10 | Cooling Tower
DDC04 | binaryInput | 11 | sts_fan_on_off_01 | Cooling Tower-3 Fan-1 Run Status | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 009 | GL 04 00 02 B7 0 009 | 9 | Cooling Tower
DDC04 | binaryInput | 12 | sts_fan_on_off_02 | Cooling Tower-4 Fan-1 Run Status | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 00A | GL 04 00 02 B7 0 00A | 10 | Cooling Tower
DDC04 | binaryInput | 13 | sts_level_switch_high_01 | Cooling Tower-1 Level Switch (High) | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 00B | GL 04 00 01 B7 0 00B | 11 | Cooling Tower
DDC04 | binaryInput | 14 | sts_level_switch_low_01 | Cooling Tower-1 Level Switch (Low) | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 00C | GL 04 00 01 B7 0 00C | 12 | Cooling Tower
DDC04 | binaryInput | 15 | sts_level_switch_high_02 | Cooling Tower-2 Level Switch (High) | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 00D | GL 04 00 01 B7 0 00D | 13 | Cooling Tower
DDC04 | binaryInput | 16 | sts_level_switch_low_02 | Cooling Tower-2 Level Switch (Low) | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 00E | GL 04 00 01 B7 0 00E | 14 | Cooling Tower
DDC04_01 | binaryInput | 1 | sts_fan_auto_manual_01 | Cooling Tower-1 Fan-1 Auto/Manual Status | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 00F | GL 04 00 01 B7 0 00F | 15 | Cooling Tower
DDC04_01 | binaryInput | 2 | sts_fan_auto_manual_02 | Cooling Tower-2 Fan-1 Auto/Manual Status | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 010 | GL 04 00 01 B7 0 010 | 16 | Cooling Tower
DDC04_01 | binaryInput | 3 | sts_fan_auto_manual_01 | Cooling Tower-3 Fan-1 Auto/Manual Status | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 00F | GL 04 00 02 B7 0 00F | 15 | Cooling Tower
DDC04_01 | binaryInput | 4 | sts_fan_auto_manual_02 | Cooling Tower-4 Fan-1 Auto/Manual Status | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 010 | GL 04 00 02 B7 0 010 | 16 | Cooling Tower
DDC04_01 | binaryInput | 5 | alm_fan_trip_01 | Cooling Tower-1 Fan-1 Trip Status | Hardpoint | GL | 04 | 00 | 01 | B7 | A | 011 | GL 04 00 01 B7 A 011 | 17 | Cooling Tower
DDC04_01 | binaryInput | 6 | alm_fan_trip_02 | Cooling Tower-2 Fan-1 Trip Status | Hardpoint | GL | 04 | 00 | 01 | B7 | A | 012 | GL 04 00 01 B7 A 012 | 18 | Cooling Tower
DDC04_01 | binaryInput | 7 | alm_fan_trip_01 | Cooling Tower-3 Fan-1 Trip Status | Hardpoint | GL | 04 | 00 | 02 | B7 | A | 011 | GL 04 00 02 B7 A 011 | 17 | Cooling Tower
DDC04_01 | binaryInput | 8 | alm_fan_trip_02 | Cooling Tower-4 Fan-1 Trip Status | Hardpoint | GL | 04 | 00 | 02 | B7 | A | 012 | GL 04 00 02 B7 A 012 | 18 | Cooling Tower
DDC04_02 | binaryInput | 1 | sts_inlet_vlv_on_off_01 | Cooling Tower-1 Inlet-1 isolation valves Open/Close Status | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 013 | GL 04 00 01 B7 0 013 | 19 | Cooling Tower
DDC04_02 | binaryInput | 2 | sts_inlet_vlv_on_off_02 | Cooling Tower-2 Inlet-1 isolation valves Open/Close Status | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 014 | GL 04 00 01 B7 0 014 | 20 | Cooling Tower
DDC04_02 | binaryInput | 3 | sts_outlet_vlv_on_off_01 | Cooling Tower-1 Outlet-1 isolation valves Open/Close Status | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 015 | GL 04 00 01 B7 0 015 | 21 | Cooling Tower
DDC04_02 | binaryInput | 4 | sts_outlet_vlv_on_off_02 | Cooling Tower-2 Outlet-1 isolation valves Open/Close Status | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 016 | GL 04 00 01 B7 0 016 | 22 | Cooling Tower
DDC04_02 | binaryInput | 5 | sts_inlet_vlv_on_off_01 | Cooling Tower-3 Inlet-1 isolation valves Open/Close Status | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 013 | GL 04 00 02 B7 0 013 | 19 | Cooling Tower
DDC04_02 | binaryInput | 6 | sts_inlet_vlv_on_off_02 | Cooling Tower-4 Inlet-1 isolation valves Open/Close Status | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 014 | GL 04 00 02 B7 0 014 | 20 | Cooling Tower
DDC04_02 | binaryInput | 7 | sts_outlet_vlv_on_off_01 | Cooling Tower-3 Outlet-1 isolation valves Open/Close Status | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 015 | GL 04 00 02 B7 0 015 | 21 | Cooling Tower
DDC04_02 | binaryInput | 8 | sts_outlet_vlv_on_off_02 | Cooling Tower-4 Outlet-1 isolation valves Open/Close Status | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 016 | GL 04 00 02 B7 0 016 | 22 | Cooling Tower
DDC04_03 | binaryOutput | 1 | cmd_inlet_vlv_on_off_01 | Cooling Tower-1 Inlet-1 isolation valves Open/Close Command | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 017 | GL 04 00 01 B7 0 017 | 23 | Cooling Tower
DDC04_03 | binaryOutput | 2 | cmd_inlet_vlv_on_off_02 | Cooling Tower-2 Inlet-1 isolation valves Open/Close Command | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 018 | GL 04 00 01 B7 0 018 | 24 | Cooling Tower
DDC04_03 | binaryOutput | 3 | cmd_outlet_vlv_on_off_01 | Cooling Tower-1 Outlet-1 isolation valves Open/Close Command | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 019 | GL 04 00 01 B7 0 019 | 25 | Cooling Tower
DDC04_03 | binaryOutput | 4 | cmd_outlet_vlv_on_off_02 | Cooling Tower-2 Outlet-1 isolation valves Open/Close Command | Hardpoint | GL | 04 | 00 | 01 | B7 | 0 | 01A | GL 04 00 01 B7 0 01A | 26 | Cooling Tower
DDC04_03 | binaryOutput | 5 | cmd_inlet_vlv_on_off_01 | Cooling Tower-3 Inlet-1 isolation valves Open/Close Command | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 017 | GL 04 00 02 B7 0 017 | 23 | Cooling Tower
DDC04_03 | binaryOutput | 6 | cmd_inlet_vlv_on_off_02 | Cooling Tower-4 Inlet-1 isolation valves Open/Close Command | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 018 | GL 04 00 02 B7 0 018 | 24 | Cooling Tower
DDC04_03 | binaryOutput | 7 | cmd_outlet_vlv_on_off_01 | Cooling Tower-3 Outlet-1 isolation valves Open/Close Command | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 019 | GL 04 00 02 B7 0 019 | 25 | Cooling Tower
DDC04_03 | binaryOutput | 8 | cmd_outlet_vlv_on_off_02 | Cooling Tower-4 Outlet-1 isolation valves Open/Close Command | Hardpoint | GL | 04 | 00 | 02 | B7 | 0 | 01A | GL 04 00 02 B7 0 01A | 26 | Cooling Tower
DDC05 | analogInput | 1 | sts_fan_vfd_frequency_01 | Cooling Tower-5 Fan-1 VFD Speed Feedback | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 001 | GL 05 00 03 B7 0 001 | 1 | Cooling Tower
DDC05 | analogOutput | 1 | cmd_fan_vfd_frequency_01 | Cooling Tower-5 Fan-1 VFD Speed Control | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 002 | GL 05 00 03 B7 0 002 | 2 | Cooling Tower
DDC05 | binaryOutput | 1 | cmd_fan_on_off_01 | Cooling Tower-5 Fan-1 VFD On/Off Command | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 003 | GL 05 00 03 B7 0 003 | 3 | Cooling Tower
DDC05 | analogInput | 2 | sts_fan_vfd_frequency_02 | Cooling Tower-6 Fan-1 VFD Speed Feedback | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 004 | GL 05 00 03 B7 0 004 | 4 | Cooling Tower
DDC05 | analogOutput | 2 | cmd_fan_vfd_frequency_02 | Cooling Tower-6 Fan-1 VFD Speed Control | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 005 | GL 05 00 03 B7 0 005 | 5 | Cooling Tower
DDC05 | binaryOutput | 2 | cmd_fan_on_off_02 | Cooling Tower-6 Fan-1 VFD On/Off Command | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 006 | GL 05 00 03 B7 0 006 | 6 | Cooling Tower
DDC05 | analogInput | 3 | par_sump_temp_01 | Cooling Tower-5 Sump Temperature-1 | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 007 | GL 05 00 03 B7 0 007 | 7 | Cooling Tower
DDC05 | binaryOutput | 3 | cmd_outlet_vlv_on_off_01 | Cooling Tower-5 Outlet-1 isolation valves Open/Close Command | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 019 | GL 05 00 03 B7 0 019 | 25 | Cooling Tower
DDC05 | analogInput | 4 | par_sump_temp_02 | Cooling Tower-6 Sump Temperature-1 | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 008 | GL 05 00 03 B7 0 008 | 8 | Cooling Tower
DDC05 | binaryOutput | 4 | cmd_outlet_vlv_on_off_02 | Cooling Tower-6 Outlet-1 isolation valves Open/Close Command | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 01A | GL 05 00 03 B7 0 01A | 26 | Cooling Tower
DDC05 | binaryInput | 5 | sts_fan_on_off_01 | Cooling Tower-5 Fan-1 Run Status | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 009 | GL 05 00 03 B7 0 009 | 9 | Cooling Tower
DDC05 | binaryOutput | 5 | cmd_inlet_vlv_on_off_01 | Cooling Tower-5 Inlet-1 isolation valves Open/Close Command | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 017 | GL 05 00 03 B7 0 017 | 23 | Cooling Tower
DDC05 | binaryInput | 6 | sts_fan_on_off_02 | Cooling Tower-6 Fan-1 Run Status | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 00A | GL 05 00 03 B7 0 00A | 10 | Cooling Tower
DDC05 | binaryOutput | 6 | cmd_inlet_vlv_on_off_02 | Cooling Tower-6 Inlet-1 isolation valves Open/Close Command | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 018 | GL 05 00 03 B7 0 018 | 24 | Cooling Tower
DDC05 | binaryInput | 7 | sts_outlet_vlv_on_off_01 | Cooling Tower-5 Outlet-1 isolation valves Open/Close Status | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 015 | GL 05 00 03 B7 0 015 | 21 | Cooling Tower
DDC05 | binaryInput | 8 | sts_outlet_vlv_on_off_02 | Cooling Tower-6 Outlet-1 isolation valves Open/Close Status | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 016 | GL 05 00 03 B7 0 016 | 22 | Cooling Tower
DDC05 | binaryInput | 9 | sts_fan_auto_manual_01 | Cooling Tower-5 Fan-1 Auto/Manual Status | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 00F | GL 05 00 03 B7 0 00F | 15 | Cooling Tower
DDC05 | binaryInput | 10 | sts_fan_auto_manual_02 | Cooling Tower-6 Fan-1 Auto/Manual Status | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 010 | GL 05 00 03 B7 0 010 | 16 | Cooling Tower
DDC05 | binaryInput | 11 | alm_fan_trip_01 | Cooling Tower-5 Fan-1 Trip Status | Hardpoint | GL | 05 | 00 | 03 | B7 | A | 011 | GL 05 00 03 B7 A 011 | 17 | Cooling Tower
DDC05 | binaryInput | 12 | alm_fan_trip_02 | Cooling Tower-6 Fan-1 Trip Status | Hardpoint | GL | 05 | 00 | 03 | B7 | A | 012 | GL 05 00 03 B7 A 012 | 18 | Cooling Tower
DDC05 | binaryInput | 13 | sts_level_switch_high_01 | Cooling Tower-3 Level Switch (High) | Hardpoint | GL | 05 | 00 | 02 | B7 | 0 | 00B | GL 05 00 02 B7 0 00B | 11 | Cooling Tower
DDC05 | binaryInput | 14 | sts_level_switch_low_01 | Cooling Tower-3 Level Switch (Low) | Hardpoint | GL | 05 | 00 | 02 | B7 | 0 | 00C | GL 05 00 02 B7 0 00C | 12 | Cooling Tower
DDC05_01 | binaryInput | 1 | sts_inlet_vlv_on_off_01 | Cooling Tower-5 Inlet-1 isolation valves Open/Close Status | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 013 | GL 05 00 03 B7 0 013 | 19 | Cooling Tower
DDC05_01 | binaryInput | 2 | sts_inlet_vlv_on_off_02 | Cooling Tower-6 Inlet-1 isolation valves Open/Close Status | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 014 | GL 05 00 03 B7 0 014 | 20 | Cooling Tower
DDC05_01 | binaryInput | 3 | sts_level_switch_high_02 | Cooling Tower-4 Level Switch (High) | Hardpoint | GL | 05 | 00 | 02 | B7 | 0 | 00D | GL 05 00 02 B7 0 00D | 13 | Cooling Tower
DDC05_01 | binaryInput | 4 | sts_level_switch_low_02 | Cooling Tower-4 Level Switch (Low) | Hardpoint | GL | 05 | 00 | 02 | B7 | 0 | 00E | GL 05 00 02 B7 0 00E | 14 | Cooling Tower
DDC05_01 | binaryInput | 5 | sts_level_switch_high_01 | Cooling Tower-5 Level Switch (High) | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 00B | GL 05 00 03 B7 0 00B | 11 | Cooling Tower
DDC05_01 | binaryInput | 6 | sts_level_switch_low_01 | Cooling Tower-5 Level Switch (Low) | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 00C | GL 05 00 03 B7 0 00C | 12 | Cooling Tower
DDC05_01 | binaryInput | 7 | sts_level_switch_high_02 | Cooling Tower-6 Level Switch (High) | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 00D | GL 05 00 03 B7 0 00D | 13 | Cooling Tower
DDC05_01 | binaryInput | 8 | sts_level_switch_low_02 | Cooling Tower-6 Level Switch (Low) | Hardpoint | GL | 05 | 00 | 03 | B7 | 0 | 00E | GL 05 00 03 B7 0 00E | 14 | Cooling Tower
DDC06 | binaryInput | 1 | sts_on_off_00 | Exhaust Fan-1 Run Status | Hardpoint | GL | 06 | 00 | 01 | A6 | 0 | 001 | GL 06 00 01 A6 0 001 | 1 | Exhaust Fan
DDC06 | binaryOutput | 1 | cmd_on_off_00 | Exhaust Fan-1 On/Off Command | Hardpoint | GL | 06 | 00 | 01 | A6 | 0 | 002 | GL 06 00 01 A6 0 002 | 2 | Exhaust Fan
DDC06 | binaryInput | 2 | sts_on_off_00 | Exhaust Fan-2 Run Status | Hardpoint | GL | 06 | 00 | 02 | A6 | 0 | 001 | GL 06 00 02 A6 0 001 | 1 | Exhaust Fan
DDC06 | binaryOutput | 2 | cmd_on_off_00 | Exhaust Fan-2 On/Off Command | Hardpoint | GL | 06 | 00 | 02 | A6 | 0 | 002 | GL 06 00 02 A6 0 002 | 2 | Exhaust Fan
DDC06 | binaryInput | 3 | sts_on_off_00 | Exhaust Fan-3 Run Status | Hardpoint | GL | 06 | 00 | 03 | A6 | 0 | 001 | GL 06 00 03 A6 0 001 | 1 | Exhaust Fan
DDC06 | binaryOutput | 3 | cmd_on_off_00 | Exhaust Fan-3 On/Off Command | Hardpoint | GL | 06 | 00 | 03 | A6 | 0 | 002 | GL 06 00 03 A6 0 002 | 2 | Exhaust Fan
DDC06 | binaryInput | 4 | sts_on_off_00 | Exhaust Fan-4 Run Status | Hardpoint | GL | 06 | 00 | 04 | A6 | 0 | 001 | GL 06 00 04 A6 0 001 | 1 | Exhaust Fan
DDC06 | binaryOutput | 4 | cmd_on_off_00 | Exhaust Fan-4 On/Off Command | Hardpoint | GL | 06 | 00 | 04 | A6 | 0 | 002 | GL 06 00 04 A6 0 002 | 2 | Exhaust Fan
DDC06 | binaryInput | 5 | alm_trip_00 | Exhaust Fan-1 Trip Status | Hardpoint | GL | 06 | 00 | 01 | A6 | A | 004 | GL 06 00 01 A6 A 004 | 4 | Exhaust Fan
DDC06 | binaryInput | 6 | alm_trip_00 | Exhaust Fan-2 Trip Status | Hardpoint | GL | 06 | 00 | 02 | A6 | A | 004 | GL 06 00 02 A6 A 004 | 4 | Exhaust Fan
DDC06 | binaryInput | 7 | alm_trip_00 | Exhaust Fan-3 Trip Status | Hardpoint | GL | 06 | 00 | 03 | A6 | A | 004 | GL 06 00 03 A6 A 004 | 4 | Exhaust Fan
DDC06 | binaryInput | 8 | alm_trip_00 | Exhaust Fan-4 Trip Status | Hardpoint | GL | 06 | 00 | 04 | A6 | A | 004 | GL 06 00 04 A6 A 004 | 4 | Exhaust Fan
DDC06 | binaryInput | 9 | sts_auto_manual_00 | Exhaust Fan-1 Auto/Manual Status | Hardpoint | GL | 06 | 00 | 01 | A6 | 0 | 003 | GL 06 00 01 A6 0 003 | 3 | Exhaust Fan
DDC06 | binaryInput | 10 | sts_auto_manual_00 | Exhaust Fan-2 Auto/Manual Status | Hardpoint | GL | 06 | 00 | 02 | A6 | 0 | 003 | GL 06 00 02 A6 0 003 | 3 | Exhaust Fan
DDC06 | binaryInput | 11 | sts_auto_manual_00 | Exhaust Fan-3 Auto/Manual Status | Hardpoint | GL | 06 | 00 | 03 | A6 | 0 | 003 | GL 06 00 03 A6 0 003 | 3 | Exhaust Fan
DDC06 | binaryInput | 12 | sts_auto_manual_00 | Exhaust Fan-4 Auto/Manual Status | Hardpoint | GL | 06 | 00 | 04 | A6 | 0 | 003 | GL 06 00 04 A6 0 003 | 3 | Exhaust Fan
DDC07 | analogValue | 1 | sts_evap_leaving_temp_00 | CH_01_Chiller_Evap Leaving Temp | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 009 | GL 07 00 01 B0 0 009 | 9 | Chiller
DDC07 | analogValue | 2 | par_evap_entering_temp_00 | CH_01_Chiller_Evap Entering Temp | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 00A | GL 07 00 01 B0 0 00A | 10 | Chiller
DDC07 | analogValue | 3 | par_suction_pressure_00 | CH_01_Chiller_Evaporator Pressure | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 00B | GL 07 00 01 B0 0 00B | 11 | Chiller
DDC07 | analogValue | 4 | par_discharge_pressure_00 | CH_01_Chiller_Condensor Pressure | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 00C | GL 07 00 01 B0 0 00C | 12 | Chiller
DDC07 | analogValue | 5 | par_comp_oil_pressure_00 | CH_01_Chiller_ Oil Differential Pressure | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 00D | GL 07 00 01 B0 0 00D | 13 | Chiller
DDC07 | analogValue | 6 | par_cond_leaving_temp_00 | CH_01_Chiller_Cond Leaving Temp | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 00E | GL 07 00 01 B0 0 00E | 14 | Chiller
DDC07 | analogValue | 7 | par_cond_entering_temp_00 | CH_01_Chiller_Cond Entering Temp | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 00F | GL 07 00 01 B0 0 00F | 15 | Chiller
DDC07 | analogValue | 8 | par_percent_load_00 | CH_01_Chiller_% Load | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 010 | GL 07 00 01 B0 0 010 | 16 | Chiller
DDC07 | analogValue | 9 | par_vsd_current_01 | CH_01_Chiller_VSD Phase A output Current | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 011 | GL 07 00 01 B0 0 011 | 17 | Chiller
DDC07 | analogValue | 10 | par_vsd_current_02 | CH_01_Chiller_VSD Phase B output Current | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 012 | GL 07 00 01 B0 0 012 | 18 | Chiller
DDC07 | analogValue | 11 | par_vsd_current_03 | CH_01_Chiller_VSD Phase C output Current | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 013 | GL 07 00 01 B0 0 013 | 19 | Chiller
DDC07 | analogValue | 12 | par_discharge_temp_00 | CH_01 Discharge Temperature | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 014 | GL 07 00 01 B0 0 014 | 20 | Chiller
DDC07 | analogValue | 13 | par_oil_temp_00 | CH_01_Chiller_Oil Sump Temprature | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 015 | GL 07 00 01 B0 0 015 | 21 | Chiller
DDC07 | analogValue | 14 | par_operating_hours_00 | CH_01_Chiller_operating hours | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 016 | GL 07 00 01 B0 0 016 | 22 | Chiller
DDC07 | analogValue | 15 | par_comp_num_starts_00 | CH_01_Chiller_Number Starts | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 017 | GL 07 00 01 B0 0 017 | 23 | Chiller
DDC07 | binaryValue | 16 | sts_chiller_panel_00 | CH_01_Chiller_Panel stop Switch | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 018 | GL 07 00 01 B0 0 018 | 24 | Chiller
DDC07 | binaryValue | 17 | sts_evap_flow_00 | CH_01_Chiller_Evap Flow Switch | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 019 | GL 07 00 01 B0 0 019 | 25 | Chiller
DDC07 | binaryValue | 18 | sts_cond_flow_00 | CH_01_Chiller_Cond Flow Switch | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 01A | GL 07 00 01 B0 0 01A | 26 | Chiller
DDC07 | binaryValue | 19 | alm_unit_safety_code_00 | CH_01_Chiller_Unit safety fault code Alarm | Softpoint | GL | 07 | 00 | 01 | B0 | A | 01B | GL 07 00 01 B0 A 01B | 27 | Chiller
DDC07 | binaryValue | 20 | alm_unit_cycling_code_00 | CH_01_Chiller_Unit cycling fault code Alarm | Softpoint | GL | 07 | 00 | 01 | B0 | A | 01C | GL 07 00 01 B0 A 01C | 28 | Chiller
DDC07 | analogValue | 21 | par_operating_code_00 | CH_01_Chiller_operation code | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 01D | GL 07 00 01 B0 0 01D | 29 | Chiller
DDC07 | analogValue | 22 | par_chilled_liqid_low_temp_00 | CH_01_Chiller_Leaving chilled Liquid low | Softpoint | GL | 07 | 00 | 01 | B0 | 0 | 01E | GL 07 00 01 B0 0 01E | 30 | Chiller
DDC07 | analogValue | 23 | sts_evap_leaving_temp_00 | CH_02_Chiller_Evap Leaving Temp | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 009 | GL 07 00 02 B0 0 009 | 9 | Chiller
DDC07 | analogValue | 24 | par_evap_entering_temp_00 | CH_02_Chiller_Evap Entering Temp | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 00A | GL 07 00 02 B0 0 00A | 10 | Chiller
DDC07 | analogValue | 25 | par_suction_pressure_00 | CH_02_Chiller_Evaporator Pressure | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 00B | GL 07 00 02 B0 0 00B | 11 | Chiller
DDC07 | analogValue | 26 | par_discharge_pressure_00 | CH_02_Chiller_Condensor Pressure | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 00C | GL 07 00 02 B0 0 00C | 12 | Chiller
DDC07 | analogValue | 27 | par_comp_oil_pressure_00 | CH_02_Chiller_ Oil Differential Pressure | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 00D | GL 07 00 02 B0 0 00D | 13 | Chiller
DDC07 | analogValue | 28 | par_cond_leaving_temp_00 | CH_02_Chiller_Cond Leaving Temp | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 00E | GL 07 00 02 B0 0 00E | 14 | Chiller
DDC07 | analogValue | 29 | par_cond_entering_temp_00 | CH_02_Chiller_Cond Entering Temp | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 00F | GL 07 00 02 B0 0 00F | 15 | Chiller
DDC07 | analogValue | 30 | par_percent_load_00 | CH_02_Chiller_% Load | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 010 | GL 07 00 02 B0 0 010 | 16 | Chiller
DDC07 | analogValue | 31 | par_vsd_current_01 | CH_02_Chiller_VSD Phase A output Current | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 011 | GL 07 00 02 B0 0 011 | 17 | Chiller
DDC07 | analogValue | 32 | par_vsd_current_02 | CH_02_Chiller_VSD Phase B output Current | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 012 | GL 07 00 02 B0 0 012 | 18 | Chiller
DDC07 | analogValue | 33 | par_vsd_current_03 | CH_02_Chiller_VSD Phase C output Current | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 013 | GL 07 00 02 B0 0 013 | 19 | Chiller
DDC07 | analogValue | 34 | par_discharge_temp_00 | CH_02 Discharge Temperature | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 014 | GL 07 00 02 B0 0 014 | 20 | Chiller
DDC07 | analogValue | 35 | par_oil_temp_00 | CH_02_Chiller_Oil Sump Temprature | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 015 | GL 07 00 02 B0 0 015 | 21 | Chiller
DDC07 | analogValue | 36 | par_operating_hours_00 | CH_02_Chiller_operating hours | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 016 | GL 07 00 02 B0 0 016 | 22 | Chiller
DDC07 | analogValue | 37 | par_comp_num_starts_00 | CH_02_Chiller_Number Starts | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 017 | GL 07 00 02 B0 0 017 | 23 | Chiller
DDC07 | binaryValue | 38 | sts_chiller_panel_00 | CH_02_Chiller_Panel stop Switch | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 018 | GL 07 00 02 B0 0 018 | 24 | Chiller
DDC07 | binaryValue | 39 | sts_evap_flow_00 | CH_02_Chiller_Evap Flow Switch | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 019 | GL 07 00 02 B0 0 019 | 25 | Chiller
DDC07 | binaryValue | 40 | sts_cond_flow_00 | CH_02_Chiller_Cond Flow Switch | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 01A | GL 07 00 02 B0 0 01A | 26 | Chiller
DDC07 | binaryValue | 41 | alm_unit_safety_code_00 | CH_02_Chiller_Unit safety fault code Alarm | Softpoint | GL | 07 | 00 | 02 | B0 | A | 01B | GL 07 00 02 B0 A 01B | 27 | Chiller
DDC07 | binaryValue | 42 | alm_unit_cycling_code_00 | CH_02_Chiller_Unit cycling fault code Alarm | Softpoint | GL | 07 | 00 | 02 | B0 | A | 01C | GL 07 00 02 B0 A 01C | 28 | Chiller
DDC07 | analogValue | 43 | par_operating_code_00 | CH_02_Chiller_operation code | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 01D | GL 07 00 02 B0 0 01D | 29 | Chiller
DDC07 | analogValue | 44 | par_chilled_liqid_low_temp_00 | CH_02_Chiller_Leaving chilled Liquid low | Softpoint | GL | 07 | 00 | 02 | B0 | 0 | 01E | GL 07 00 02 B0 0 01E | 30 | Chiller
DDC07 | analogValue | 45 | sts_evap_leaving_temp_00 | CH_03_Chiller_Evap Leaving Temp | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 009 | GL 07 00 03 B0 0 009 | 9 | Chiller
DDC07 | analogValue | 46 | par_evap_entering_temp_00 | CH_03_Chiller_Evap Entering Temp | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 00A | GL 07 00 03 B0 0 00A | 10 | Chiller
DDC07 | analogValue | 47 | par_suction_pressure_00 | CH_03_Chiller_Evaporator Pressure | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 00B | GL 07 00 03 B0 0 00B | 11 | Chiller
DDC07 | analogValue | 48 | par_discharge_pressure_00 | CH_03_Chiller_Condensor Pressure | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 00C | GL 07 00 03 B0 0 00C | 12 | Chiller
DDC07 | analogValue | 49 | par_comp_oil_pressure_00 | CH_03_Chiller_ Oil Differential Pressure | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 00D | GL 07 00 03 B0 0 00D | 13 | Chiller
DDC07 | analogValue | 50 | par_cond_leaving_temp_00 | CH_03_Chiller_Cond Leaving Temp | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 00E | GL 07 00 03 B0 0 00E | 14 | Chiller
DDC07 | analogValue | 51 | par_cond_entering_temp_00 | CH_03_Chiller_Cond Entering Temp | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 00F | GL 07 00 03 B0 0 00F | 15 | Chiller
DDC07 | analogValue | 52 | par_percent_load_00 | CH_03_Chiller_% Load | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 010 | GL 07 00 03 B0 0 010 | 16 | Chiller
DDC07 | analogValue | 53 | par_vsd_current_01 | CH_03_Chiller_VSD Phase A output Current | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 011 | GL 07 00 03 B0 0 011 | 17 | Chiller
DDC07 | analogValue | 54 | par_vsd_current_02 | CH_03_Chiller_VSD Phase B output Current | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 012 | GL 07 00 03 B0 0 012 | 18 | Chiller
DDC07 | analogValue | 55 | par_vsd_current_03 | CH_03_Chiller_VSD Phase C output Current | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 013 | GL 07 00 03 B0 0 013 | 19 | Chiller
DDC07 | analogValue | 56 | par_discharge_temp_00 | CH_03 Discharge Temperature | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 014 | GL 07 00 03 B0 0 014 | 20 | Chiller
DDC07 | analogValue | 57 | par_oil_temp_00 | CH_03_Chiller_Oil Sump Temprature | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 015 | GL 07 00 03 B0 0 015 | 21 | Chiller
DDC07 | analogValue | 58 | par_operating_hours_00 | CH_03_Chiller_operating hours | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 016 | GL 07 00 03 B0 0 016 | 22 | Chiller
DDC07 | analogValue | 59 | par_comp_num_starts_00 | CH_03_Chiller_Number Starts | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 017 | GL 07 00 03 B0 0 017 | 23 | Chiller
DDC07 | binaryValue | 60 | sts_chiller_panel_00 | CH_03_Chiller_Panel stop Switch | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 018 | GL 07 00 03 B0 0 018 | 24 | Chiller
DDC07 | binaryValue | 61 | sts_evap_flow_00 | CH_03_Chiller_Evap Flow Switch | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 019 | GL 07 00 03 B0 0 019 | 25 | Chiller
DDC07 | binaryValue | 62 | sts_cond_flow_00 | CH_03_Chiller_Cond Flow Switch | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 01A | GL 07 00 03 B0 0 01A | 26 | Chiller
DDC07 | binaryValue | 63 | alm_unit_safety_code_00 | CH_03_Chiller_Unit safety fault code Alarm | Softpoint | GL | 07 | 00 | 03 | B0 | A | 01B | GL 07 00 03 B0 A 01B | 27 | Chiller
DDC07 | binaryValue | 64 | alm_unit_cycling_code_00 | CH_03_Chiller_Unit cycling fault code Alarm | Softpoint | GL | 07 | 00 | 03 | B0 | A | 01C | GL 07 00 03 B0 A 01C | 28 | Chiller
DDC07 | analogValue | 65 | par_operating_code_00 | CH_03_Chiller_operation code | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 01D | GL 07 00 03 B0 0 01D | 29 | Chiller
DDC07 | analogValue | 66 | par_chilled_liqid_low_temp_00 | CH_03_Chiller_Leaving chilled Liquid low | Softpoint | GL | 07 | 00 | 03 | B0 | 0 | 01E | GL 07 00 03 B0 0 01E | 30 | Chiller
DDC07 | analogValue | 67 | par_avg_current_00 | Pump_01_Current | Softpoint | GL | 07 | 00 | 01 | B2 | 0 | 007 | GL 07 00 01 B2 0 007 | 7 | Primary Variable pump
DDC07 | analogValue | 68 | par_avg_power_00 | Pump_01_Power | Softpoint | GL | 07 | 00 | 01 | B2 | 0 | 008 | GL 07 00 01 B2 0 008 | 8 | Primary Variable pump
DDC07 | analogValue | 69 | par_avg_voltage_00 | Pump_01_Voltage | Softpoint | GL | 07 | 00 | 01 | B2 | 0 | 009 | GL 07 00 01 B2 0 009 | 9 | Primary Variable pump
DDC07 | analogValue | 70 | par_energy_00 | Pump_01 _Energy kWH | Softpoint | GL | 07 | 00 | 01 | B2 | 0 | 00A | GL 07 00 01 B2 0 00A | 10 | Primary Variable pump
DDC07 | analogValue | 71 | par_frequency_00 | Pump_01_Frequency | Softpoint | GL | 07 | 00 | 01 | B2 | 0 | 00B | GL 07 00 01 B2 0 00B | 11 | Primary Variable pump
DDC07 | analogValue | 72 | par_speed_00 | Pump_01_Speed | Softpoint | GL | 07 | 00 | 01 | B2 | 0 | 00C | GL 07 00 01 B2 0 00C | 12 | Primary Variable pump
DDC07 | analogValue | 73 | par_avg_current_00 | Pump_02_Current | Softpoint | GL | 07 | 00 | 02 | B2 | 0 | 007 | GL 07 00 02 B2 0 007 | 7 | Primary Variable pump
DDC07 | analogValue | 74 | par_avg_power_00 | Pump_02_Power | Softpoint | GL | 07 | 00 | 02 | B2 | 0 | 008 | GL 07 00 02 B2 0 008 | 8 | Primary Variable pump
DDC07 | analogValue | 75 | par_avg_voltage_00 | Pump_02_Voltage | Softpoint | GL | 07 | 00 | 02 | B2 | 0 | 009 | GL 07 00 02 B2 0 009 | 9 | Primary Variable pump
DDC07 | analogValue | 76 | par_energy_00 | Pump_02 _Energy kWH | Softpoint | GL | 07 | 00 | 02 | B2 | 0 | 00A | GL 07 00 02 B2 0 00A | 10 | Primary Variable pump
DDC07 | analogValue | 77 | par_frequency_00 | Pump_02_Frequency | Softpoint | GL | 07 | 00 | 02 | B2 | 0 | 00B | GL 07 00 02 B2 0 00B | 11 | Primary Variable pump
DDC07 | analogValue | 78 | par_speed_00 | Pump_02_Speed | Softpoint | GL | 07 | 00 | 02 | B2 | 0 | 00C | GL 07 00 02 B2 0 00C | 12 | Primary Variable pump
DDC07 | analogValue | 79 | par_avg_current_00 | Pump_03_Current | Softpoint | GL | 07 | 00 | 03 | B2 | 0 | 007 | GL 07 00 03 B2 0 007 | 7 | Primary Variable pump
DDC07 | analogValue | 80 | par_avg_power_00 | Pump_03_Power | Softpoint | GL | 07 | 00 | 03 | B2 | 0 | 008 | GL 07 00 03 B2 0 008 | 8 | Primary Variable pump
DDC07 | analogValue | 81 | par_avg_voltage_00 | Pump_03_Voltage | Softpoint | GL | 07 | 00 | 03 | B2 | 0 | 009 | GL 07 00 03 B2 0 009 | 9 | Primary Variable pump
DDC07 | analogValue | 82 | par_energy_00 | Pump_03 _Energy kWH | Softpoint | GL | 07 | 00 | 03 | B2 | 0 | 00A | GL 07 00 03 B2 0 00A | 10 | Primary Variable pump
DDC07 | analogValue | 83 | par_frequency_00 | Pump_03_Frequency | Softpoint | GL | 07 | 00 | 03 | B2 | 0 | 00B | GL 07 00 03 B2 0 00B | 11 | Primary Variable pump
DDC07 | analogValue | 84 | par_speed_00 | Pump_03_Speed | Softpoint | GL | 07 | 00 | 03 | B2 | 0 | 00C | GL 07 00 03 B2 0 00C | 12 | Primary Variable pump
DDC07 | analogValue | 85 | btu_meter_actual_flow_00 | Btu_Meter_Actual_Flow | Softpoint | GL | 07 | 00 | 01 | C0 | 0 | 00F | GL 07 00 01 C0 0 00F | 15 | Header
DDC07 | analogValue | 86 | btu_meter_actual_power_00 | Btu_Meter_Actual_Power | Softpoint | GL | 07 | 00 | 01 | C0 | 0 | 010 | GL 07 00 01 C0 0 010 | 16 | Header
DDC07 | analogValue | 87 | btu_meter_energy_consump_00 | Btu_Meter_Energy_Consump | Softpoint | GL | 07 | 00 | 01 | C0 | 0 | 011 | GL 07 00 01 C0 0 011 | 17 | Header
DDC07 | analogValue | 88 | btu_meter_inlet_temp_00 | Btu_Meter_Inlet_Temp | Softpoint | GL | 07 | 00 | 01 | C0 | 0 | 012 | GL 07 00 01 C0 0 012 | 18 | Header
DDC07 | analogValue | 89 | btu_meter_outlet_temp_00 | Btu_Meter_Outlet_Temp | Softpoint | GL | 07 | 00 | 01 | C0 | 0 | 013 | GL 07 00 01 C0 0 013 | 19 | Header
DDC07 | analogValue | 90 | par_avg_current_01 | Cooling_Tower1_Fan_1_Current | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 01B | GL 07 00 01 B7 0 01B | 27 | Cooling Tower
DDC07 | analogValue | 91 | par_avg_power_01 | Cooling_Tower1_Fan_1_Power | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 01C | GL 07 00 01 B7 0 01C | 28 | Cooling Tower
DDC07 | analogValue | 92 | par_avg_voltage_01 | Cooling_Tower1_Fan_1_Voltage | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 01D | GL 07 00 01 B7 0 01D | 29 | Cooling Tower
DDC07 | analogValue | 93 | par_energy_kwh_01 | Cooling_Tower1_Fan_1 _Energy kWH | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 01E | GL 07 00 01 B7 0 01E | 30 | Cooling Tower
DDC07 | analogValue | 94 | par_frequency_01 | Cooling_Tower1_Fan_1_Frequency | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 01F | GL 07 00 01 B7 0 01F | 31 | Cooling Tower
DDC07 | analogValue | 95 | par_speed_01 | Cooling_Tower1_Fan_1_Speed | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 020 | GL 07 00 01 B7 0 020 | 32 | Cooling Tower
DDC07 | analogValue | 96 | par_avg_current_02 | Cooling_Tower2_Fan_01_Current | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 021 | GL 07 00 01 B7 0 021 | 33 | Cooling Tower
DDC07 | analogValue | 97 | par_avg_power_02 | Cooling_Tower2_Fan_01_Power | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 022 | GL 07 00 01 B7 0 022 | 34 | Cooling Tower
DDC07 | analogValue | 98 | par_avg_voltage_02 | Cooling_Tower2_Fan_01_Voltage | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 023 | GL 07 00 01 B7 0 023 | 35 | Cooling Tower
DDC07 | analogValue | 99 | par_energy_kwh_02 | Cooling_Tower2_Fan_01 _Energy kWH | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 024 | GL 07 00 01 B7 0 024 | 36 | Cooling Tower
DDC07 | analogValue | 100 | par_frequency_02 | Cooling_Tower2_Fan_01_Frequency | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 025 | GL 07 00 01 B7 0 025 | 37 | Cooling Tower
DDC07 | analogValue | 101 | par_speed_02 | Cooling_Tower2_Fan_01_Speed | Softpoint | GL | 07 | 00 | 01 | B7 | 0 | 026 | GL 07 00 01 B7 0 026 | 38 | Cooling Tower
DDC07 | analogValue | 102 | par_avg_current_01 | Cooling_Tower3_Fan_01_Current | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 01B | GL 07 00 02 B7 0 01B | 27 | Cooling Tower
DDC07 | analogValue | 103 | par_avg_power_01 | Cooling_Tower3_Fan_01_Power | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 01C | GL 07 00 02 B7 0 01C | 28 | Cooling Tower
DDC07 | analogValue | 104 | par_avg_voltage_01 | Cooling_Tower3_Fan_01_Voltage | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 01D | GL 07 00 02 B7 0 01D | 29 | Cooling Tower
DDC07 | analogValue | 105 | par_energy_kwh_01 | Cooling_Tower3_Fan_01 _Energy kWH | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 01E | GL 07 00 02 B7 0 01E | 30 | Cooling Tower
DDC07 | analogValue | 106 | par_frequency_01 | Cooling_Tower3_Fan_01_Frequency | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 01F | GL 07 00 02 B7 0 01F | 31 | Cooling Tower
DDC07 | analogValue | 107 | par_speed_01 | Cooling_Tower3_Fan_01_Speed | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 020 | GL 07 00 02 B7 0 020 | 32 | Cooling Tower
DDC07 | analogValue | 108 | par_avg_current_02 | Cooling_Tower4_Fan_01_Current | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 021 | GL 07 00 02 B7 0 021 | 33 | Cooling Tower
DDC07 | analogValue | 109 | par_avg_power_02 | Cooling_Tower4_Fan_01_Power | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 022 | GL 07 00 02 B7 0 022 | 34 | Cooling Tower
DDC07 | analogValue | 110 | par_avg_voltage_02 | Cooling_Tower4_Fan_01_Voltage | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 023 | GL 07 00 02 B7 0 023 | 35 | Cooling Tower
DDC07 | analogValue | 111 | par_energy_kwh_02 | Cooling_Tower4_Fan_01 _Energy kWH | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 024 | GL 07 00 02 B7 0 024 | 36 | Cooling Tower
DDC07 | analogValue | 112 | par_frequency_02 | Cooling_Tower4_Fan_01_Frequency | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 025 | GL 07 00 02 B7 0 025 | 37 | Cooling Tower
DDC07 | analogValue | 113 | par_speed_02 | Cooling_Tower4_Fan_01_Speed | Softpoint | GL | 07 | 00 | 02 | B7 | 0 | 026 | GL 07 00 02 B7 0 026 | 38 | Cooling Tower
DDC07 | analogValue | 114 | par_avg_current_01 | Cooling_Tower5_Fan_01_Current | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 01B | GL 07 00 03 B7 0 01B | 27 | Cooling Tower
DDC07 | analogValue | 115 | par_avg_power_01 | Cooling_Tower5_Fan_01_Power | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 01C | GL 07 00 03 B7 0 01C | 28 | Cooling Tower
DDC07 | analogValue | 116 | par_avg_voltage_01 | Cooling_Tower5_Fan_01_Voltage | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 01D | GL 07 00 03 B7 0 01D | 29 | Cooling Tower
DDC07 | analogValue | 117 | par_energy_kwh_01 | Cooling_Tower5_Fan_01 _Energy kWH | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 01E | GL 07 00 03 B7 0 01E | 30 | Cooling Tower
DDC07 | analogValue | 118 | par_frequency_01 | Cooling_Tower5_Fan_01_Frequency | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 01F | GL 07 00 03 B7 0 01F | 31 | Cooling Tower
DDC07 | analogValue | 119 | par_speed_01 | Cooling_Tower5_Fan_01_Speed | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 020 | GL 07 00 03 B7 0 020 | 32 | Cooling Tower
DDC07 | analogValue | 120 | par_avg_current_02 | Cooling_Tower6_Fan_01_Current | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 021 | GL 07 00 03 B7 0 021 | 33 | Cooling Tower
DDC07 | analogValue | 121 | par_avg_power_02 | Cooling_Tower6_Fan_01_Power | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 022 | GL 07 00 03 B7 0 022 | 34 | Cooling Tower
DDC07 | analogValue | 122 | par_avg_voltage_02 | Cooling_Tower6_Fan_01_Voltage | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 023 | GL 07 00 03 B7 0 023 | 35 | Cooling Tower
DDC07 | analogValue | 123 | par_energy_kwh_02 | Cooling_Tower6_Fan_01 _Energy kWH | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 024 | GL 07 00 03 B7 0 024 | 36 | Cooling Tower
DDC07 | analogValue | 124 | par_frequency_02 | Cooling_Tower6_Fan_01_Frequency | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 025 | GL 07 00 03 B7 0 025 | 37 | Cooling Tower
DDC07 | analogValue | 125 | par_speed_02 | Cooling_Tower6_Fan_01_Speed | Softpoint | GL | 07 | 00 | 03 | B7 | 0 | 026 | GL 07 00 03 B7 0 026 | 38 | Cooling Tower
DDC07 | analogValue | 126 | par_avg_current_00 | Condenser_Pump_01_Current | Softpoint | GL | 07 | 00 | 01 | B4 | 0 | 007 | GL 07 00 01 B4 0 007 | 7 | Condenser pump
DDC07 | analogValue | 127 | par_avg_power_00 | Condenser_Pump_01_Power | Softpoint | GL | 07 | 00 | 01 | B4 | 0 | 008 | GL 07 00 01 B4 0 008 | 8 | Condenser pump
DDC07 | analogValue | 128 | par_avg_voltage_00 | Condenser_Pump_01_Voltage | Softpoint | GL | 07 | 00 | 01 | B4 | 0 | 009 | GL 07 00 01 B4 0 009 | 9 | Condenser pump
DDC07 | analogValue | 129 | par_energy_00 | Condenser_Pump_01 _Energy kWH | Softpoint | GL | 07 | 00 | 01 | B4 | 0 | 00A | GL 07 00 01 B4 0 00A | 10 | Condenser pump
DDC07 | analogValue | 130 | par_frequency_00 | Condenser_Pump_01_Frequency | Softpoint | GL | 07 | 00 | 01 | B4 | 0 | 00B | GL 07 00 01 B4 0 00B | 11 | Condenser pump
DDC07 | analogValue | 131 | par_speed_00 | Condenser_Pump_01_Speed | Softpoint | GL | 07 | 00 | 01 | B4 | 0 | 00C | GL 07 00 01 B4 0 00C | 12 | Condenser pump
DDC07 | analogValue | 132 | par_avg_current_00 | Condenser_Pump_02_Current | Softpoint | GL | 07 | 00 | 02 | B4 | 0 | 007 | GL 07 00 02 B4 0 007 | 7 | Condenser pump
DDC07 | analogValue | 133 | par_avg_power_00 | Condenser_Pump_02_Power | Softpoint | GL | 07 | 00 | 02 | B4 | 0 | 008 | GL 07 00 02 B4 0 008 | 8 | Condenser pump
DDC07 | analogValue | 134 | par_avg_voltage_00 | Condenser_Pump_02_Voltage | Softpoint | GL | 07 | 00 | 02 | B4 | 0 | 009 | GL 07 00 02 B4 0 009 | 9 | Condenser pump
DDC07 | analogValue | 135 | par_energy_00 | Condenser_Pump_02 _Energy kWH | Softpoint | GL | 07 | 00 | 02 | B4 | 0 | 00A | GL 07 00 02 B4 0 00A | 10 | Condenser pump
DDC07 | analogValue | 136 | par_frequency_00 | Condenser_Pump_02_Frequency | Softpoint | GL | 07 | 00 | 02 | B4 | 0 | 00B | GL 07 00 02 B4 0 00B | 11 | Condenser pump
DDC07 | analogValue | 137 | par_speed_00 | Condenser_Pump_02_Speed | Softpoint | GL | 07 | 00 | 02 | B4 | 0 | 00C | GL 07 00 02 B4 0 00C | 12 | Condenser pump
DDC07 | analogValue | 138 | par_avg_current_00 | Condenser_Pump_03_Current | Softpoint | GL | 07 | 00 | 03 | B4 | 0 | 007 | GL 07 00 03 B4 0 007 | 7 | Condenser pump
DDC07 | analogValue | 139 | par_avg_power_00 | Condenser_Pump_03_Power | Softpoint | GL | 07 | 00 | 03 | B4 | 0 | 008 | GL 07 00 03 B4 0 008 | 8 | Condenser pump
DDC07 | analogValue | 140 | par_avg_voltage_00 | Condenser_Pump_03_Voltage | Softpoint | GL | 07 | 00 | 03 | B4 | 0 | 009 | GL 07 00 03 B4 0 009 | 9 | Condenser pump
DDC07 | analogValue | 141 | par_energy_00 | Condenser_Pump_03 _Energy kWH | Softpoint | GL | 07 | 00 | 03 | B4 | 0 | 00A | GL 07 00 03 B4 0 00A | 10 | Condenser pump
DDC07 | analogValue | 142 | par_frequency_00 | Condenser_Pump_03_Frequency | Softpoint | GL | 07 | 00 | 03 | B4 | 0 | 00B | GL 07 00 03 B4 0 00B | 11 | Condenser pump
DDC07 | analogValue | 143 | par_speed_00 | Condenser_Pump_03_Speed | Softpoint | GL | 07 | 00 | 03 | B4 | 0 | 00C | GL 07 00 03 B4 0 00C | 12 | Condenser pump

## Condenser_pump
Condenser Water Pump-1 VFD Feedback | sts_pump_vfd_frequency_00
Condenser Water Pump-1 run Status | sts_on_off_00
Condenser Water Pump-1 VFD Control | cmd_pump_vfd_frequency_00
Condenser Water Pump-1 VFD On/Off Command | cmd_on_off_00
Condenser Water Pump-1 Trip Status | alm_trip_00
Condenser Water Pump-1 Auto/Manual Status | sts_auto_manual_00

## Chiller
Chiller-1 Run Status | sts_on_off_00
Chiller-1 Enable/Disable Command | cmd_on_off_00
Chiller-1 Auto/Manual Status | sts_auto_manual_00
Chiller-1 Fault/Alarm Status | alm_trip_00
Chiller-1 Motorized Valve-1 Feedback | sts_bypass_vlv_01 | doubt
Chiller-1 Motorized Valve-2 Feedback | sts_bypass_vlv_02 | doubt
Chiller-1 Motorized Valve-1 Command | cmd_bypass_vlv_01 | doubt
Chiller-1 Motorized Valve-2 Command | cmd_bypass_vlv_02 | doubt

## Header
Description | Short_Names
Outside Air Temp monitoring | par_out_air_temp_00
Outside Air Relative Humidity Monitoring | par_out_air_humidity_00
CHW Common Supply Header Temperature | par_cwh_sup_temp_00
CHW Common Return Header Temperature | par_cwh_ret_temp_00
Condenser Water Supply Header Temperature | par_cdw_sup_temp_00
Condenser Water Return Header Temperature | par_cdw_ret_temp_00
Bypass Temperature | par_bypass_temp_00
Bypass Modulating Valve Feedback | sts_bypass_vlv_00
Bypass Modulating Valve Control | cmd_bypass_vlv_00
CDW Common supply header flow | par_cdw_sup_flow_00
CHW Common Supply and Return Header Pressure monitoring | par_cwh_sup_ret_pressure_00
Diff Pressure Monitoring @Main Header | par_dpt_01
Diff Pressure Monitoring @AHU Header | par_dpt_02
Decimal Meter | par_decimal_meter_00

## Exhaust_Fan
Exhaust Fan-1 Run Status | sts_on_off_00
Exhaust Fan-1 Trip Status | alm_trip_00
Exhaust Fan-1 On/Off Command | cmd_on_off_00
Exhaust Fan-1 Auto/Manual Status | sts_auto_manual_00

## Cooling_Tower
Cooling Tower-1 Fan-1 VFD Speed Feedback | sts_fan_vfd_frequency_01
Cooling Tower-1 Fan-2 VFD Speed Feedback | sts_fan_vfd_frequency_02
Cooling Tower-1 Sump Temperature-1 | par_sump_temp_01
Cooling Tower-1 Sump Temperature-2 | par_sump_temp_02
Cooling Tower-1 Fan-1 VFD Speed Control | cmd_fan_vfd_frequency_01
Cooling Tower-1 Fan-2 VFD Speed Control | cmd_fan_vfd_frequency_02
Cooling Tower-1 Fan-1 VFD On/Off Command | cmd_fan_on_off_01
Cooling Tower-1 Fan-2 VFD On/Off Command | cmd_fan_on_off_02
Cooling Tower-1 Fan-1 Run Status | sts_fan_on_off_01
Cooling Tower-1 Fan-2 Run Status | sts_fan_on_off_02
Cooling Tower-1 Level Switch (High) | sts_level_switch_high_00
Cooling Tower-1 Level Switch (Low) | sts_level_switch_low_00
Cooling Tower-1 Fan-1 Auto/Manual Status | sts_fan_auto_manual_01
Cooling Tower-1 Fan-2 Auto/Manual Status | sts_fan_auto_manual_02
Cooling Tower-1 Fan-1 Trip Status | alm_fan_trip_01
Cooling Tower-1 Fan-2 Trip Status | alm_fan_trip_02
Cooling Tower-1 Inlet-1 isolation valves Open/Close Status | sts_inlet_vlv_on_off_01
Cooling Tower-1 Inlet-2 isolation valves Open/Close Status | sts_inlet_vlv_on_off_02
Cooling Tower-1 Outlet-1 isolation valves Open/Close Status | sts_outlet_vlv_on_off_01
Cooling Tower-1 Outlet-2 isolation valves Open/Close Status | sts_outlet_vlv_on_off_02
Cooling Tower-1 Inlet-1 isolation valves Open/Close Command | cmd_inlet_vlv_on_off_01
Cooling Tower-1 Inlet-2 isolation valves Open/Close Command | cmd_inlet_vlv_on_off_02
Cooling Tower-1 Outlet-1 isolation valves Open/Close Command | cmd_outlet_vlv_on_off_01
Cooling Tower-1 Outlet-2 isolation valves Open/Close Command | cmd_outlet_vlv_on_off_02

## Primary_pump
Description | Short name
Chilled Water Pump-1 VFD Feedback | sts_pump_vfd_frequency_00
Chilled Water Pump-1 run Status | sts_on_off_00
Chilled Water Pump-1 VFD Control | cmd_pump_vfd_frequency_00
Chilled Water Pump-1 VFD On/Off Command | cmd_on_off_00
Chilled Water Pump-1 Trip Status | alm_trip_00
Chilled Water Pump-1 Auto/Manual Status | sts_auto_manual_00